## Sheet1
FORMAT I: Fatal and non-fatal accident report
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Number of Accidents during the month |  |  |  |  | Cumulative since starting of year |  | Cumulative since starting of year
Departmental |  | Outside |  |  | Departmental |  | Outside
FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH
0 | 1 | 0 | 0 | 1 | 2 | 3 | 4 | 1 | 11
FH- Fatal Human
NFH- Non Fatal Human
FA- Fatal Animal
FORMAT II: Action taken report for safety measures complied for the accidents occurred
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Sl. No. | Location of accident and details of victim | Date of occurrence | Type of accident | Cause of accident | Findings of CEI/EI /AEI | Remedies suggested by CEI/EI/AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such accidents | Amount paid as compensation
1 | K-Ist, 18 / 269, Sangam Vihar, New Delhi. | 01.11.2020 at 8:30 AM | Non-Fatal | A Non-fatal accident happened on date 01.11.2020 at K-1st, 18 / 269, Sangam Vihar, New Delhi at around 8:30 AM, when a mentally weak boy named Sh. Sunil (25 year old) came in contact of live part of HVDS system. He got flashes in his hand and taken to hospital by neighbors. Due to this incident area of K1st 18 was under breakdown and during patrolling line man got the information about this incident. Report in prescribed format is send to electrical inspector. | N.A. | N.A. | N.A. | N.A. | N.A.
2 | 66KV Bodella 1 - Paschim Vihar Ckt-2, Tower No. 4, STP DJB Keshopur Compound near Drain, Keshopur Mandi, New Delhi. | 23.11.2020 at 12:16 Hrs. | Non-Fatal | An electrical accident had occurred on 66KV Bodella 1 - Paschim Vihar Ckt on 23.11.2020 at 12:16 Hrs.during a maintenance activity in which Sh. Gori Tigga, Lineman of AMC M/S Imperial Electric Company got an electric shock when he was climbing on tower for maintenance of Ckt no.1 after confirming the nomenclature painted on both legs of tower in presence of Shri Dharam Sai (AM(O)) and Shri Amit Mudgil, (Manager) EHV TRL West. PTW was issued online ( No. PTW023112016257) from Budhella 1 66 KV S/Stn for Outgoing to Paschim Vihar Ckt No.1 O/H Transmission Line for Preventive Maintenance. Line was isolated at both ends and earthed at Bodella 1 end, line was also discharged manually at Bodella 1 before starting the work. The line was not discharged by TRL team prior to climbing on tower as a safety measure. The L/M got shocked when he throw rope for making safety arrangement because the line was charged and simultaneously Ckt no.2 got tripped from Budhella-1 Grid & Paschim Vihar Grid (Log sheet of Paschim vihar Grid attached). The victim was taken immediately to Park Hospital located near Keshopur Mandi, but, they denied admission. Then, he was taken to Deen Dayal Upadhayay Hospital located in Hari Nagar where he got primary treatment and later on referred to Safdarjung Hospital, but, due to non-availability of bed he was referred to Ram Manohar Hospital where he is currently receiving properly treatment. | N.A. | N.A. | N.A. | N.A. | N.A.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | Within Specified Time | Beyond specified time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9
Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. |  |  | - | 15069 | 15069 | 15069 | 0 | 15069 | 0
Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. |  |  |  | 999 | 999 | 999 | 0 | 999 | 0
Continuous power supply failure requiring replacement of distribution transformer. |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) |  |  |  | 4786 | 4786 | 4786 | 0 | 4786 | 0
Continuous Schduled Power Outage |  |  |  | 371 | 371 | 371 | 0 | 371 | 0
Replacement of Burnt Meter or Stolen Meter |  |  | 45 | 2049 | 2094 | 1789 | 156 | 1945 | 104
FORMAT IV: Quality of Power Supply
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | Within Specified Time | Beyond specified time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Local Problem |  | 4 hours | 0 | 436 | 436 | 436 | 0 | 436 | 0
Tap setting of transformer
Repair of Distribution Line/transformer/ capacitor
Installation and Up gradation of High Tension/ Low Tension System
FORMAT V: Complaint about meters
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaint lodged for accuracy test of meter-Fast |  | Within fifteen days | 1788 | 0 | 1788 | 147 | 8 | 155 | 1633
Complaint lodged for accuracy test of meter-Slow |  | Within fifteen days | 0 | 0 | 0 | 0 | 0 | 0 | 0
Complaint lodged for defective / stuck meter |  | Within fifteen days | 314 | 0 | 314 | 140 | 39 | 179 | 135
Complaint lodged for burnt meter |  | Restoration of supply with 3hrs and meter to be replaced within 3days. | 453 | 0 | 453 | 153 | 62 | 215 | 238
Complaint lodged for stolen meter |  |  | 5 | 0 | 5 | 1 | 0 | 1 | 4
FORMAT VI: New Connections / Additional Load, where power suppply can be provided from existing network
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
New Connection where no RoW or road Cutting permission is required |  | 7 days | 4528 | 0 | 4528 | 275 | 35 | 310 | 4218
New Connection where RoW or road Cutting permission is required |  | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Connection where no RoW or road Cutting permission is required |  | 7 days | 101 | 0 | 101 | 3 | 0 | 3 | 98
New Connection where RoW or road Cutting permission is required |  | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT VII: Applications for New Connections / Additional Load, where power supply requires extension of distribution system.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
1. Electrified Areas (where extension of line upto five poles is required) |  | 15 days from receipt of payment
2. Electrified areas (where extension of lines or augmentation of Distribution Transformer capacity where peak load of transformer has reached 90% of its rated capacity. |  | Within 2 months from receipt of payment
3. Electrified areas (where new distribtion transformer is required) |  | Within 4 months from receipt of payment
4. Electrified Areas (where existing 11 KV network needs to be augmented) |  | 15 days
5. Electrified Areas (where existing 66/33 kV substation needs to be augmented) |  | 15 days
New Connections |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional Load |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT VIII: Connection in un-electrified areas
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Un-Electrified Areas (Where connection from nearby existing network is possible) |  | Within 4 months from Commission's approval | 0 | 0 | 0 | 0 | 0 | 0 | 0
Un-Electrified Areas/ Green Field Projects (Where new network is to be laid or grid station needs to be established) |  | Within 12 months from Commission's approval | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT IX: Transfer of Consumer's connection and conversion of services.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Transfer of Name |  | Within two billing cycles of acceptance of application or clearing of dues whichever is later | 56 | 0 | 56 | 3 | 0 | 3 | 53
Load Reduction |  | Within ten days of acceptance of application, shall be effective from next billing cycle | 65 | 0 | 65 | 4 | 0 | 4 | 61
Change of Category |  | As per Regulation 17 (5) | 405 | 0 | 405 | 0 | 4 | 4 | 401
Incase connection is denied after receipt of payment against demand note |  | - | 42 | 0 | 42 | 15 | 27 | 42 | 0
Connection energized through Loop |  | As per Regulation 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
If notice towards downward if any is not sent |  | 31st May of Financial year | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT X: Complaints about consumer's bills, disconnection, reconnection of supply.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaints on billing |  | Only one bill in a Financial Year | 1219 | 0 | 1219 | 36 | 13 | 49 | 1170
Final bill for vacation of premises / change of occupance. |  | 5 days | 290 | 0 | 290 | 4 | 2 | 6 | 284
Non payment of dues by the consumer |  | 15 days | 8 | 0 | 8 | 0 | 0 | 0 | 8
Request for reconnection |  | 24hrs | 64 | 0 | 64 | 13 | 15 | 28 | 36
Consumer wanting disconnection |  | 5 days | 850 | 0 | 850 | 310 | 92 | 402 | 448
FORMAT XI: Failure of Distribution Transformer
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
No. of Distribution transformers at the beginning of the month |  | No. of Distribution transformers added during the month |  | Total number of distribution transformers |  | Number of Distribution transformers failed |  | % Failure rate of distribution transformers
1 |  | 2 |  | 3=1+2 |  | 4 |  | 5=(4)*100/(3)%
7558 |  | 50 |  | 7608 |  | 1 |  | 1.314%
Note: | Only 3 phase transformers considered>=400 kVA
Only New transformers added in the system is considered against point no. 2
Only O&M failure considered
FORMAT XII: Failure of Power Transformer
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
No. of power transformers at the beginning of the month |  | No. of power transformers added during the month |  | Total number of power transformers |  | Number of power transformers failed |  | % Failure rate of power transformers
1 |  | 2 |  | 3=1+2 |  | 4 |  | 5=(4)*100/(3)%
260 |  | 1 |  | 261 |  | 0 |  | 0%
FORMAT XIII: Summary of Overall Standards of Performance.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Sl. No. | Service area |  | Overall Standards of Performance | Total Cases Received / Reported (A) |  | Complaints Attended (B) |  | Standard of Performance Achieved (C)
[6 empty] | Within Specified Time | Beyond specified time
1. Power Supply Failure
(i) | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. |  | 15069 |  | 15069 | 0 | 100%
(ii) | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. |  | 999 |  | 999 | 0 | 100%
(iii) | Continuous power supply failure requiring replacement of distribution transformer. | Continuous power supply failure requiring replacement of distribution transformer. |  | 0 |  | 0 | 0 | 100%
(iv) | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above |  | 4786 |  | 4786 | 0 | 100%
(v) | Continuous scheduled power outages | Continuous scheduled power outages |  | 371 |  | 371 | 0 | 100%
(vi) | Replacement of burnt meter | Replacement of burnt meter or stolen meter |  | 2094 |  | 1789 | 156 | 85.43%
Period of Scheduled Outage
2 | Maximum duration in a single stretch |  |  | 07H:10M
| Restoration of supply by 6:00 PM |  |  | ALL
3 | Faults in street light maintained by the licensee |  |  | 1810 |  | 1808 | 2 | 99.89%
Reliability Indices
4 | SAIFI |  |  | 0.26
| SAIDI |  |  | 0.16
| CAIDI |  |  | 0.61538
5 | Frequency variation |  |  | 0 |  | 0 | 0 | 0
6 | Voltage imbalance |  |  | 0 |  | 0 | 0 | 0
7 | Percentage billing mistakes |  |  | 0 |  | 0 | 0 | 0
* New method used for reliabilty index calculation*
FORMAT XIV: Compensation Details
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Sl. No. | Event |  | Compensation specified for violation of standard |  | Claimed |  | Payable/Paid
[5 empty] | No. of Cases | Amount Claimed | No. of cases in which compensation is payable | Amount of compensation payable in (Rs.) | Amount of compensation paid in (Rs.)
1 | Electricity connections
(i) | Electrified Areas | Electrified Areas | 1.5% of the demand charges deposited by consumer for each day of default.
(ii) | Augmentation Required | Augmentation Required | 1.5% of the demand charges deposited by consumer for each day of default | 1.5% of the demand charges deposited by consumer for each day of default
(iii) | Un-electrified Areas | Un-electrified Areas | 1% of the amount deposited by developer/applicants per day of default. | 1% of the amount deposited by developer/applicants per day of default.
(iv) | Connection denied after receipt of payment against demand note | Connection denied after receipt of payment against demand note | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment. | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment.
(v) | Connection energized through loop | Connection energized through loop | Rs. 500 per kW of sanctioned/ contract demand | Rs. 500 per kW of sanctioned/ contract demand
2 | Transfer of Name | Transfer of Name | Rs. 100 for each day of default. | Rs. 100 for each day of default.
3 | Load Reduction | Load Reduction | Rs. 100 for each day of default | Rs. 100 for each day of default
4 | Notice for downward revision of load | Notice for downward revision of load | Rs. 500 for each case | Rs. 500 for each case
5 | Change of category | Change of category | Rs. 100 for each day of default | Rs. 100 for each day of default
6 | Complaints in billing | Complaints in billing | 10% of excess amount billed | 10% of excess amount billed
7 | Replacement of meters | Replacement of meters | Rs.50 for each day of default | Rs.50 for each day of default
8 | Fault in street light maintained by the Licensee | Fault in street light maintained by the Licensee | Rs. 75 for each day of default | Rs. 75 for each day of default
9 | Voltage fluctuations and complainsts | Voltage fluctuations and complainsts
10 | Power Supply Failure | Power Supply Failure
11 | Total | Total
FORMAT XV: Unauthorized Use of Electricity
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
No. of Cases Booked |  | No. of Cases where UUE is established by the Licensee |  | No. of cases where appeal filed by the consumer before the Appellate Authority |  | No. of cases decided by the Appellate Authority in favor of the Licensee |  | No. of cases decided by the Appellate Authority in the favor of the consumer
23 |  | 46 |  | 0 |  | 0 |  | 0
FORMAT XVI: Theft of Electricity
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
No. of Cases Booked |  | No. of complaints filed by the Licensee in Police Station |  | No. of cases in which judgement delivered by the Special Court |  | No. of cases decided by the Special Court in favor of Licensee |  | No. of cases decided by the Special Court in favor of Consumer
1817 |  | 973 |  | 0 |  | 0 |  | 0

## FORMAT I
FORMAT I: Fatal and non-fatal accident report
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Number of Accidents during the month |  |  |  |  | Cumulative since starting of year |  | Cumulative since starting of year
Departmental |  | Outside |  |  | Departmental |  | Outside
FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH
0 | 1 | 0 | 0 | 1 | 2 | 3 | 4 | 1 | 11
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FH- Fatal Human
NFH- Non Fatal Human
FA- Fatal Animal

## FORMAT II
FORMAT II: Action taken report for safety measures complied for the accidents occurred
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Sl. No. | Location of accident and details of victim | Date of occurrence | Type of accident | Cause of accident | Findings of CEI/EI /AEI | Remedies suggested by CEI/EI/AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such accidents | Amount paid as compensation
1 | K-Ist, 18 / 269, Sangam Vihar, New Delhi. | 01.11.2020 at 8:30 AM | Non-Fatal | A Non-fatal accident happened on date 01.11.2020 at K-1st, 18 / 269, Sangam Vihar, New Delhi at around 8:30 AM, when a mentally weak boy named Sh. Sunil (25 year old) came in contact of live part of HVDS system. He got flashes in his hand and taken to hospital by neighbors. Due to this incident area of K1st 18 was under breakdown and during patrolling line man got the information about this incident. Report in prescribed format is send to electrical inspector. | N.A. | N.A. | N.A. | N.A. | N.A.
2 | 66KV Bodella 1 - Paschim Vihar Ckt-2, Tower No. 4, STP DJB Keshopur Compound near Drain, Keshopur Mandi, New Delhi. | 23.11.2020 at 12:16 Hrs. | Non-Fatal | An electrical accident had occurred on 66KV Bodella 1 - Paschim Vihar Ckt on 23.11.2020 at 12:16 Hrs.during a maintenance activity in which Sh. Gori Tigga, Lineman of AMC M/S Imperial Electric Company got an electric shock when he was climbing on tower for maintenance of Ckt no.1 after confirming the nomenclature painted on both legs of tower in presence of Shri Dharam Sai (AM(O)) and Shri Amit Mudgil, (Manager) EHV TRL West. PTW was issued online ( No. PTW023112016257) from Budhella 1 66 KV S/Stn for Outgoing to Paschim Vihar Ckt No.1 O/H Transmission Line for Preventive Maintenance. Line was isolated at both ends and earthed at Bodella 1 end, line was also discharged manually at Bodella 1 before starting the work. The line was not discharged by TRL team prior to climbing on tower as a safety measure. The L/M got shocked when he throw rope for making safety arrangement because the line was charged and simultaneously Ckt no.2 got tripped from Budhella-1 Grid & Paschim Vihar Grid (Log sheet of Paschim vihar Grid attached). The victim was taken immediately to Park Hospital located near Keshopur Mandi, but, they denied admission. Then, he was taken to Deen Dayal Upadhayay Hospital located in Hari Nagar where he got primary treatment and later on referred to Safdarjung Hospital, but, due to non-availability of bed he was referred to Ram Manohar Hospital where he is currently receiving properly treatment. | N.A. | N.A. | N.A. | N.A. | N.A.
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT III
FORMAT III: Action taken report for safety measures complied for the accidents occurred
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | Within Specified Time | Beyond specified time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9
Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. | 0 | - | 15069 | 15069 | 15069 | 0 | 15069 | 0
Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. | 0 | 0 | 999 | 999 | 999 | 0 | 999 | 0
Continuous power supply failure requiring replacement of distribution transformer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) | 0 | 0 | 4786 | 4786 | 4786 | 0 | 4786 | 0
Continuous Schduled Power Outage | 0 | 0 | 371 | 371 | 371 | 0 | 371 | 0
Replacement of Burnt Meter or Stolen Meter | 0 | 45 | 2049 | 2094 | 1789 | 156 | 1945 | 104

## FORMAT IV
FORMAT IV: Quality of Power Supply
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | Within Specified Time | Beyond specified time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Local Problem | 4 hours | 0 | 436 | 436 | 436 | 0 | 436 | 0
Tap setting of transformer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair of Distribution Line/transformer/ capacitor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installation and Up gradation of High Tension/ Low Tension System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT V
FORMAT V: Complaint about meters
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaint lodged for accuracy test of meter-Fast | Within fifteen days | 1788 | 0 | 1788 | 147 | 8 | 155 | 1633
Complaint lodged for accuracy test of meter-Slow | Within fifteen days | 0 | 0 | 0 | 0 | 0 | 0 | 0
Complaint lodged for defective / stuck meter | Within fifteen days | 314 | 0 | 314 | 140 | 39 | 179 | 135
Complaint lodged for burnt meter | Restoration of supply with 3hrs and meter to be replaced within 3days. | 453 | 0 | 453 | 153 | 62 | 215 | 238
Complaint lodged for stolen meter |  | 5 | 0 | 5 | 1 | 0 | 1 | 4

## FORMAT VI
FORMAT VI: New Connections / Additional Load, where power suppply can be provided from existing network
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
New Connection where no RoW or road Cutting permission is required | 7 days | 4528 | 0 | 4528 | 275 | 35 | 310 | 4218
New Connection where RoW or road Cutting permission is required | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Connection where no RoW or road Cutting permission is required | 7 days | 101 | 0 | 101 | 3 | 0 | 3 | 98
New Connection where RoW or road Cutting permission is required | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT VII
FORMAT VII: Applications for New Connections / Additional Load, where power supply requires extension of distribution system.
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
1. Electrified Areas (where extension of line upto five poles is required) | 15 days from receipt of payment | 0 | 0 | 0 | 0 | 0 | 0 | 0
2. Electrified areas (where extension of lines or augmentation of Distribution Transformer capacity where peak load of transformer has reached 90% of its rated capacity. | Within 2 months from receipt of payment | 0 | 0 | 0 | 0 | 0 | 0 | 0
3. Electrified areas (where new distribtion transformer is required) | Within 4 months from receipt of payment | 0 | 0 | 0 | 0 | 0 | 0 | 0
4. Electrified Areas (where existing 11 KV network needs to be augmented) | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Electrified Areas (where existing 66/33 kV substation needs to be augmented) | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Connections |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional Load |  | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT VIII
FORMAT VIII: Connection in un-electrified areas
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Un-Electrified Areas (Where connection from nearby existing network is possible) | Within 4 months from Commission's approval | 0 | 0 | 0 | 0 | 0 | 0 | 0
Un-Electrified Areas/ Green Field Projects (Where new network is to be laid or grid station needs to be established) | Within 12 months from Commission's approval | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT IX
FORMAT IX: Transfer of Consumer's connection and conversion of services.
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Transfer of Name | Within two billing cycles of acceptance of application or clearing of dues whichever is later | 56 | 0 | 56 | 3 | 0 | 3 | 53
Load Reduction | Within ten days of acceptance of application, shall be effective from next billing cycle | 65 | 0 | 65 | 4 | 0 | 4 | 61
Change of Category | As per Regulation 17 (5) | 405 | 0 | 405 | 0 | 4 | 4 | 401
Incase connection is denied after receipt of payment against demand note | - | 42 | 0 | 42 | 15 | 27 | 42 | 0
Connection energized through Loop | As per Regulation 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
If notice towards downward if any is not sent | 31st May of Financial year | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT X
FORMAT X: Complaints about consumer's bills, disconnection, reconnection of supply.
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaints on billing | Only one bill in a Financial Year | 1219 | 0 | 1219 | 36 | 13 | 49 | 1170
Final bill for vacation of premises / change of occupance. | 5 days | 290 | 0 | 290 | 4 | 2 | 6 | 284
Non payment of dues by the consumer | 15 days | 8 | 0 | 8 | 0 | 0 | 0 | 8
Request for reconnection | 24hrs | 64 | 0 | 64 | 13 | 15 | 28 | 36
Consumer wanting disconnection | 5 days | 850 | 0 | 850 | 310 | 92 | 402 | 448

## FORMAT XI
FORMAT XI: Failure of Distribution Transformer
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
No. of Distribution transformers at the beginning of the month |  | No. of Distribution transformers added during the month | Total number of distribution transformers | Failed transformer | % Failure rate of distribution transformers
1 |  | 2 | 3=1+2 | 4 | 5=(4)*100/(3)%
7558 |  | 50 | 7608 | 1 | 1.314%
0 |  | 0 | 0 | 0 | 0
0 |  | 0 | 0 | 0 | 0
0 |  | 0 | 0 | 0 | 0
Note: | Only 3 phase transformers considered>=400 kVA
Only New transformers added in the system is considered against point no. 2
Only O&M failure considered

## FORMAT XII
FORMAT XI: Failure of Power Transformer
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
No. of power transformers at the beginning of the month | No. of power transformers added during the month | Total number of power transformers | Number of power transformers failed | % Failure rate of power transformers
1 | 2 | 3=1+2 | 4 | 5=(4)*100/(3)%
260 | 1 | 261 | 0 | 0%
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0

## FORMAT XIII
FORMAT XIII: Summary of Overall Standards of Performance.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Sl. No. | Service area |  | Overall Standards of Performance | Total Cases Received / Reported (A) | Complaints Attended (B) |  | Standard of Performance Achieved (C)
[5 empty] | Within Specified Time | Beyond specified time
1. Power Supply Failure
(i) | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. |  | 15069 | 15069 | 0 | 100%
(ii) | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. |  | 999 | 999 | 0 | 100%
(iii) | Continuous power supply failure requiring replacement of distribution transformer. | Continuous power supply failure requiring replacement of distribution transformer. |  | 0 | 0 | 0 | 100%
(iv) | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above |  | 4786 | 4786 | 0 | 100%
(v) | Continuous scheduled power outages | Continuous scheduled power outages |  | 371 | 371 | 0 | 100%
(vi) | Replacement of burnt meter | Replacement of burnt meter or stolen meter |  | 2094 | 1789 | 156 | 85.43%
Period of Scheduled Outage
2 | Maximum duration in a single stretch |  |  | 07H:10M | 0 | 0 | 0%
| Restoration of supply by 6:00 PM |  |  | ALL | 0 | 0 | 0%
3 | Faults in street light maintained by the licensee |  |  | 1810 | 1808 | 2 | 99.89%
Reliability Indices
4 | SAIFI |  |  | 0.26 | 0 | 0 | 0
| SAIDI |  |  | 0.16 | 0 | 0 | 0
| CAIDI |  |  | 0.61538 | 0 | 0 | 0
5 | Frequency variation |  |  | 0 | 0 | 0 | 0
6 | Voltage imbalance |  |  | 0 | 0 | 0 | 0
7 | Percentage billing mistakes |  |  | 0 | 0 | 0 | 0

## FORMAT XIV
FORMAT XIV: Compensation Details
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2020-11-01
Year: |  | 2020
Sl. No. | Event |  | Compensation specified for violation of standard |  | Claimed |  | Payable/Paid
[5 empty] | No. of Cases | Amount Claimed | No. of cases in which compensation is payable | Amount of compensation payable in (Rs.) | Amount of compensation paid in (Rs.)
1 | Electricity connections |  |  |  | 0 | 0 | 0 | 0 | 0
(i) | Electrified Areas | Electrified Areas | 1.5% of the demand charges deposited by consumer for each day of default. |  | 0 | 0 | 0 | 0 | 0
(ii) | Augmentation Required | Augmentation Required | 1.5% of the demand charges deposited by consumer for each day of default | 1.5% of the demand charges deposited by consumer for each day of default | 0 | 0 | 0 | 0 | 0
(iii) | Un-electrified Areas | Un-electrified Areas | 1% of the amount deposited by developer/applicants per day of default. | 1% of the amount deposited by developer/applicants per day of default. | 0 | 0 | 0 | 0 | 0
(iv) | Connection denied after receipt of payment against demand note | Connection denied after receipt of payment against demand note | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment. | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment. | 0 | 0 | 0 | 0 | 0
(v) | Connection energized through loop | Connection energized through loop | Rs. 500 per kW of sanctioned/ contract demand | Rs. 500 per kW of sanctioned/ contract demand | 0 | 0 | 0 | 0 | 0
2 | Transfer of Name | Transfer of Name | Rs. 100 for each day of default. | Rs. 100 for each day of default. | 0 | 0 | 0 | 0 | 0
3 | Load Reduction | Load Reduction | Rs. 100 for each day of default | Rs. 100 for each day of default | 0 | 0 | 0 | 0 | 0
4 | Notice for downward revision of load | Notice for downward revision of load | Rs. 500 for each case | Rs. 500 for each case | 0 | 0 | 0 | 0 | 0
5 | Change of category | Change of category | Rs. 100 for each day of default | Rs. 100 for each day of default | 0 | 0 | 0 | 0 | 0
6 | Complaints in billing | Complaints in billing | 10% of excess amount billed | 10% of excess amount billed | 0 | 0 | 0 | 0 | 0
7 | Replacement of meters | Replacement of meters | Rs.50 for each day of default | Rs.50 for each day of default | 0 | 0 | 0 | 0 | 0
8 | Fault in street light maintained by the Licensee | Fault in street light maintained by the Licensee | Rs. 75 for each day of default | Rs. 75 for each day of default | 0 | 0 | 0 | 0 | 0
9 | Voltage fluctuations and complainsts | Voltage fluctuations and complainsts |  |  | 0 | 0 | 0 | 0 | 0
10 | Power Supply Failure | Power Supply Failure |  |  | 0 | 0 | 0 | 0 | 0
11 | Total | Total |  |  | 0 | 0 | 0 | 0 | 0

## FORMAT XV
FORMAT XV: Unauthorized Use of Electricity
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
No. of Cases Booked | No. of Cases where UUE is established by the Licensee | No. of cases where appeal filed by the consumer before the Appellate Authority | No. of cases decided by the Appellate Authority in favor of the Licensee | No. of cases decided by the Appellate Authority in the favor of the consumer
23 | 46 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0

## FORMAT XVI
FORMAT XVI: Theft of Electricity
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2020-11-01
Year: | 2020
No. of Cases Booked | No. of complaints filed by the Licensee in Police Station | No. of cases in which judgement delivered by the Special Court | No. of cases decided by the Special Court in favor of Licensee | No. of cases decided by the Special Court in favor of Consumer
1817 | 973 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0