SCOPE OF TURNKEY EXECUTION

FOR

66kV/11 kV & 33kV/11 kV SUBSTATION

ALONGWITH

ASSOCIATED INFEEDS & OUTGOING FEEDERS

Contents

1.0	INTENT	3

2.0	BIDDER’S SCOPE	3

2.1	DESIGN & ENGINEERING	3

2.1.1	CODES AND STANDARDS	3

2.1.2	SERVICE CONDITIONS	4

2.1.3	SYSTEM PARAMETERS	4

2.2	PACKAGE -1 - LAXMI NAGAR GRID S/S WITH INFEED AND OUTGOING	5

2.2.1	INFEED SITE DETAIL	5

2.2.2	INFEED SCOPE OF SUPPLY	5

2.2.3	INFEED SCOPE OF WORK	7

2.2.4	GRID S/S DETAIL	11

2.2.5	GRID S/S SCOPE OF SUPPLY	11

2.2.6	GRID S/S SCOPE OF WORK	15

2.2.7	GRID S/S SLD	19

2.2.8	OUTGOING SCOPE OF SUPPLY	20

2.2.9	OUTGOING SCOPE OF WORK	21

2.3	PACKAGE -2 - HARGOBIND ENCLAVE GRID S/S WITH INFEED AND OUTGOING	24

2.3.1	INFEED SITE DETAIL	24

2.3.2	INFEED SCOPE OF SUPPLY	24

2.3.3	INFEED SCOPE OF WORK	25

2.3.4	INFEED GENERAL ARRANGEMENT DRAWING	10

2.3.5	GRID S/S DETAIL	28

2.3.6	GRID S/S SCOPE OF SUPPLY	28

2.3.7	GRID S/S SCOPE OF WORK	32

2.3.8	GRID S/S SLD	36

2.3.9	OUTGOING SCOPE OF SUPPLY	37

2.3.10	OUTGOING SCOPE OF WORK	38

2.4	PACKAGE-3 - MANDOLI JAIL COMPLEX GRID S/S WITH INFEED AND OUTGOING	42

2.4.1	INFEED SITE DETAIL	42

2.4.2	INFEED SCOPE OF SUPPLY	42

2.4.3	INFEED SCOPE OF WORK	43

2.4.4	GRID S/S DETAIL	46

2.4.5	GRID S/S SCOPE OF SUPPLY	46

2.4.6	GRID S/S SCOPE OF WORK	50

2.4.7	GRID S/S SLD	54

2.4.8	OUTGOING SCOPE OF SUPPLY	55

2.4.9	OUTGOING SCOPE OF WORK	56

2.5	SCOPE DEMARCATION	59

2.6	DOCUMENTATION	61

3.0	APPROVED MAKE LIST	63

# INTENT

- This document defines the scope for turnkey execution of new grids and associated infeed and outgoing feeders at

- 33 kV /11kV Hargobind Enclave Grid S/S

- 33 kV /11kV Laxmi nagar Grid S/S

- 66 kV /11 kV Mandoli Jail Complex Grid S/S

- This document shall be read in conjunction with all technical documents enclosed in tender. In event of any contradiction between tender documents, the most stringent one shall govern.

# BIDDER’S SCOPE

- Bidder’s Scope includes design, engineering, manufacture, shop testing, inspection, packing, dispatch, supply, loading, unloading, storage at site, assembly, erection, civil, structural, architectural work, complete pre-commissioning checks, testing & commissioning at site, obtaining statutory clearance & certification from Electrical Inspector and handing over of equipment covered under scope of this document to BSES Yamuna Power Ltd.

- Details are given in subsequent sections. It shall be noted that project execution shall ensure uninterrupted operation of grid. All quantities mentioned in scope of Supply/ work are estimated quantities. Actual quantities may vary as per site requirement. ETC of all supplied items shall be in Bidders scope

- Bidder shall depute its representative at site to assess the condition of existing infrastructure in detail prior to submission of bid.

## DESIGN & ENGINEERING

- Detailed design and engineering of complete project as per tender requirements shall be in bidder’s scope.

- General guidelines for design are given below

### CODES AND STANDARDS

- The bidder shall comply with latest Indian/International standard and CEA regulations.

- Refer respective equipment specification for applicable standards.

### SERVICE CONDITIONS

|  | Average grade atmosphere | Heavily polluted, Dry |
| --- | --- | --- |
|  | Maximum altitude above sea level | 1000M |
|  | Ambient air temperature | Highest 50Deg C, Average 40Deg C |
|  | Minimum ambient air temperature | 0 Deg C |
|  | Relative Humidity | 100% |
|  | Rainfall | 750mm concentrated in four months |
|  | Seismic Condition | Zone IV |
|  | Max. Relative Humidity | 100% |

### SYSTEM PARAMETERS

|  | Nominal Voltage kV | 66 | 33 | 11 |
| --- | --- | --- | --- | --- |
|  | Rated voltage kV | 72.5 | 36 | 12 |
|  | Power Frequency (kV rms) with stand voltage | 140 | 70 | 28 |
|  | Basic Insulation Level KVp | 325 | 170 | 75 |
|  | Rated Frequency Hz | 50±5% | 50±5% | 50±5% |
|  | System Neutral Earthing | Solidly Grounded | Solidly Grounded | Solidly Grounded |

## PACKAGE -1 - LAXMI NAGAR GRID S/S WITH INFEED AND OUTGOING

- Site detail, Scope of Supply and Scope of Work of Infeed, Grid S/S and Outgoing Feeder are given below

### INFEED SITE DETAIL

- Infeed site detail may be fetched from table below

- Each circuit consists of two run cable

| S. No | Circuit Detail | Cable length (Meter) |
| --- | --- | --- |
|  | DTL 220 kV PPG to BYPL Laxmi Nagar Grid - 2 Run (LILO in existing KKD-PPG ckt near PPG end - Refer LILO 1 in General layout drawing) | 2600 |
|  | DTL 220 kV Preet Vihar to BYPL Laxmi Nagar Grid - 2 Run (LILO in existing KKD-PPG ckt near PPG end) Refer LILO 2 in General layout drawing) | 2600 |
|  | DTL 220 kV Preet Vihar to BYPL Laxmi Nagar Grid - 2 Run (LILO in existing KKD-PPG ckt near Preet Vihar end) - Refer LILO 3 in General layout drawing) | 1600 |
|  | DTL 220 kV Preet Vihar to BYPL Karkardooma Grid - 2 Run (LILO in existing KKD-PPG ckt near Preet Vihar end) - Refer LILO 4 in General layout drawing) | 1600 |
|  | BYPL Laxmi Nagar to Mother Dairy Substation - 2 Run | 1600 |

### INFEED SCOPE OF SUPPLY

| S No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Cable 33 kV 3Cx400 sq mm | Meter | 10000 |
|  | Cable End Termination kit- Indoor Suitable for 33 kV 3Cx400 sq mm cable (Make- Raychem/3M) | No's | 2 |
|  | Cable End Termination kit for GIS panel suitable for 33 kV 3Cx400 sq mm cable (Make- Raychem/3M) | No's | 10 |
|  | Cable straight through joint kit Suitable for 33 kV 3Cx400 sq mm cable(Make- Raychem/3M) | No's | 50 |
|  | Precast RCC (1:2:4) cable cover 600x550x50 mm (used where 4 cable runs in one trench) | No's | 5950 |
|  | Precast RCC (1:2:4) cable cover 600x300x50 mm (used where 2 cable runs in one trench) | No's | 2267 |
|  | HDPE PIPE 200 MM DIA PN4 PE 80 | Meter | 3500 |
|  | HDPE Pipe Collar 200 mm | No's | 583 |
|  | Weather and acid resistant PVC warning tape of 150mm width 300 micron thick Yellow colour with desired Red/Black lettering | Meter | 2465 |
|  | Route indicating stone at every 50 meter circuit length and Joint indicating stones at every cable joint location | No's | 93 |
|  | Galvanized Channel, Angle, Beam and other Structural steel with hardwares for all structures including cable support Structure | MT | 1 |
|  | Fine Sand | Cubic meter | 775 |
|  | End Cap for Cable 33 KV AL 3X400 Sqmm XLPE | No's | 100 |
|  | Optical Fiber cable 48F a. 2 Runs in Laxmi Nagar - Mother Dairy circuit b. 2 Runs in DTL PPG - Laxmi Nagar circuit | Meter | 4200 |
|  | Duct for Optical Fibre Cable (40mm) | Meter | 4200 |
|  | Collar for optical fiber cable duct | No's | 42 |
|  | Optical Fiber cable splice enclosure for jointing of optical fiber cable | No's | 5 |
|  | Fibre optic cable end termination distribution box | No's | 8 |
|  | Cable armour- earth link box without SVL | No's | 12 |
|  | HDPE cleat with hardware's suitable for 33 kV 3Cx400 sq mm cable | No's | 24 |
|  | Support insulators for mounting of cable on support structure | No's | 12 |
|  | Danger Plates | No's | 12 |
|  | Circuit Name Plate | No's | 12 |
|  | Anti Climbing device | No's | 6 |
|  | Cable Identitication Road Stud | No's | 1 |
|  | 50X6 Sq mm GI Earthing strip | MT | 1 |
|  | Aluminium Cable Identification tag with nylon string | No's | 333 |
|  | Safety barricading PVC tape | Meter | 1 |
|  | Safety barricading cone | No's | 1 |
|  | RFID based electronic buried type cable route marker for cable joints and turns having facility to feed the joint/turn related information | No's | 1 |
|  | Receiver unit for electronic cable route marker cum cable route tracer suitable with offline as well as online cable route tracing functionality | No's | 1 |
|  | Coarse sand for PCC & RCC | Cubic meter | 1 |
|  | Burnt clay Brick - First class | No's | 1 |
|  | Cement Bags 50 kg | No's | 1 |
|  | Reinforcement steel bars | MT | 1 |
|  | Construction Aggregate | Cubic meter | 1 |
|  | Optical Fiber cable loop chamber for every 300 meter of cable run | No's | 14 |
|  | Phase marking Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) | Lot | 1 |
|  | cable sheath repair 3M Scotch 2228 Rubber mastic Tape | Lot | 1 |
|  | Self-Fusing Silicone Rubber Electrical Tape 70 | Lot | 1 |
|  | Fire retardant coating for application on Power cables and Optical fiber cable | Lot | 1 |

### INFEED SCOPE OF WORK

| S.No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Surveying of cable Route, Detailed Site Plan & Profile using Ground penetration Radar System, Excavation of trial pits as per field requirement, preparation of route drawing with location of joint chambers position and finalizing the cable route in consultation with BSES Representative | Meter | 2900 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Ordinary Bituminous/C.C.Road (including dewatering if any) | Cubic meter | 939 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Dense Carpeted bituminous Road (including dewatering if any) | Cubic meter | 751 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Footpath/tile/Rajasthani Stone/Brick work (including dewatering if any) | Cubic meter | 751 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Hard Rocky Soil (including dewatering if any) | Cubic meter | 751 |
|  | Laying of XLPE cables in the excavated trench, as per BYPL Standards (Regarding Depth, Layer formation, etc). Cable rollers to be used during Laying. | Meter | 6500 |
|  | Laying of XLPE cable in HDPE Pipe in excavated trench | Meter | 2000 |
|  | Laying of cable in trenchless ducts including laying of cable and HDPE pipe using HDD machine including laying of 200 mm dia HDPE pipe PN4 PE 80 Class | Meter | 1500 |
|  | Continuous steel Barricading for all Excavated areas, till the work is completed. | Lot | 1 |
|  | Fixing of Aluminum Cable identification tags with Nylon string at every 30 Mtrs cable length | No's | 333 |
|  | Installation of straight through joints for 33 kv 3Cx400 sq mm cables by jointing kit OEM authorized jointer | No's | 50 |
|  | Installation of End Termination -indor suitable for 33kv 3Cx400 sq mm cables by jointing kit OEM authorized jointer | No's | 2 |
|  | Instalation of End Termination kit in 33 kV GIS suitable for 33 kV 3Cx400 sq mm cable by jointing kit OEM authorized jointer | No's | 10 |
|  | Digging of joint pit suitable for 33 cable joint box and covering the joint box with sand and providing protection for Ordinary bituminous road/C.C. Road | No's | 13 |
|  | Digging of joint pit suitable for 33 cable joint box and covering the joint box with sand and providing protection for Dense carpeted bituminous road. | No's | 13 |
|  | Digging of joint pit suitable for 33 cable joint box and covering the joint box with sand and providing protection for Footpath/ tile/ Rajasthani Stone / Brick Works | No's | 13 |
|  | Digging of joint pit suitable for 33 cable joint box and covering the joint box with sand and providing protection for Hard Rocky Soil. | No's | 13 |
|  | Spreading of sand forming cushion and cover around the cable | Cubic meter | 775 |
|  | Disposal of debris/surplus malba including Loading / Unloading | Cubic meter | 853 |
|  | Digging of test pits of required size( not less than 1/2 Meter Wide at site for identification of cable route) | No's | 6 |
|  | Watch and ward of complete circuit till project handover | Lot | 1 |
|  | Installation of precast RCC Cable cover | No's | 8217 |
|  | Installation of Route and Joint indicating stone marked with "BYPL 33 KV Cable Helpline No-91-11-399 99 808" | No's | 93 |
|  | Laying of PVC warning tape | Meter | 2465 |
|  | Fabrication and installation of galvanized channel, angel, Beam and other structural steel including nuts & bolts for all structures including cable support structure, drain crossing structure etc | MT | 1 |
|  | Laying of optical fiber cable in 40 mm duct including blowing and pulling | Meter | 4200 |
|  | Installation of OFC cable splice enclosure | No's | 5 |
|  | Testing of optical fiber cable after installation | Lot | 1 |
|  | Partial discharge test on complete cable length at site | Lot | 1 |
|  | VLF High voltage test & Tan Delta test on complete cable length as per relevant IEC/IEEE | Lot | 1 |
|  | Installation of Fiber optic cable distribution box for termination of fiber optic cable | No's | 8 |
|  | Installation of cable armour- earth link box without SVL including cable earthing/armour connection with grid earthing | No's | 12 |
|  | Installation, mounting and fixing of 33 kV 3Cx400 sq mm cable with termination on mounting structure/tower and fixing it with suitable HDPE cleats | No's | 24 |
|  | Installation of support insulators on cable mounting structure with misc. hardware's. | No's | 12 |
|  | Fixing of danger plate on poles including fabrication of clamps etc | No's | 12 |
|  | Fixing of circuit Name plate including fabrication of clamps etc | No's | 12 |
|  | Fixing of anti climbing device on cables mounting structures including fabrication of clamps etc | No's | 6 |
|  | Installation of Cable identification road stud | No's | 1 |
|  | Transportation of empty 33 kV cable drums from site to BSES store | No's | 50 |
|  | Laying of GI earth connecting strip of 50x6 sq mm size including required welding, painting on joints etc | MT | 1 |
|  | Submission of actual laid drawing of cable circuits including GPS coordinates of all joint in cables circuits | Lot | 1 |
|  | Cable Phasing work, Cable Phase Sequence (R,Y,B) Marking, Cable 1&2 Marking, and final connection as per Phase Sequence. | Lot | 1 |
|  | Masonry Brick work | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:1.5:3 (1 cement :1.5 coarse sand : 3 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:2:4 (1 cement :2 coarse sand : 4 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:4:8 (1 cement :4 coarse sand : 8 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Centering, shuttering including shuttering propping etc and removal of shuttering | Lot | 1 |
|  | Fabrication of reinforcement for RCC work including straightening, cutting, bending, placing in position and binding all complete thermo mechanically treated bars. | Lot | 1 |
|  | Installation of Brick as Cable Separator | No's | 1 |
|  | Installation of Optical Fiber cable loop chamber | No's | 14 |
|  | ETC of RFID marker | No's | 1 |
|  | Application of Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) on cable end termination kit | Lot | 1 |
|  | Application of 3M Scotch 2228 Rubber mastic Tape on cable straight through joint end sealing and for cable sheath repair | Lot | 1 |
|  | Application of Self-Fusing Silicone Rubber Electrical Tape 70 on cable end termination boot and lug | Lot | 1 |
|  | Application of fire retardant coating on Infeed Power cables and Optical fibre cable in yard boundary and exposed areas | Lot | 1 |

### INFEED GENERAL ARRANGEMENT DRAWING

### GRID S/S DETAIL

- 33 kV /11 kV Laxmi nagar Grid Substation is situated near  Aditi Apartment, Mother dairy Marg, IP Extension, Shahdara, Delhi 110092

### GRID S/S SCOPE OF SUPPLY

| S No. | Items | Remarks | UOM | Qty |
| --- | --- | --- | --- | --- |
|  | 33 kV GIS with Double Bus Bar Arrangement as per SLD Attached | - Arrangement also includes Bus Riser Panel wherever applicable - Line Differential Protection Relay shall be supplied as Relay 1 (Main protection) of incomer feeder for Both Receiving and Sending End. |  |  |
|  | Incomer Feeder with Line PT |  | Nos | 3 |
|  | Transformer Feeder |  | Nos | 2 |
|  | Bus Coupler |  | Nos | 1 |
|  | Bus PT |  | Nos | 2 |
|  | 25 MVA, 33 kV/11 kV Power Transformer (Including Marshalling Box and NIFPS) |  | Nos | 2 |
|  | 11 kV Switchboard | Arrangement also includes Bus Riser Panel wherever applicable |  |  |
|  | Incoming panel (with Line PT) |  | Nos | 2 |
|  | Bus Coupler Panel(Having Provision for termination of 3 x 1c x 1000sqmm cable per phase) |  | Nos | 1 |
|  | Bus PT |  | Nos | 1 |
|  | Capacitor Panel |  | Nos | 2 |
|  | Outgoing Panel |  | Nos | 12 |
|  | Station Transformer Panel |  | Nos | 1 |
|  | Earthing Truck for Bus bar Side Earthing |  | Nos | 2 |
|  | Earthing Truck for Cable bar Side Earthing |  | Nos | 2 |
|  | 33 kV Incomer (AIS) with Single Bus Bar Arrangement | - Panel has to be coupled with existing panel at Mother Dairy S/S of BYPL - Make- M/s Siemens - It also includes cabling work | Nos | 1 |
|  | 11 kV Auto Switched Capacitor Bank |  | Nos | 2 |
|  | 33 kV 3CX400 XLPE insulated, stranded aluminum conductor, PVC outer sheath Power cable | For connecting all power transformer from 33 kV Trafo panel | Lot | 1 |
|  | 11 kV 1CX1000 sqmm XLPE insulated, stranded Aluminium conductor, PVC outer sheath cable | All Power transformer to 11 kV incoming Panel | Lot | 1 |
|  | 11 kV 3CX300 sqmm XLPE insulated, stranded aluminum conductor, PVC outer sheath Power cable | For 11 kV Capacitor Bank | Lot | 1 |
|  | GIS termination kit for 33kV, 3c x 400sqmm cable | For termination at 33kV GIS | Nos | 2 |
|  | End Termination kit for 33kV, 3CX400 sqmm Cable | For connecting cable to the bushing of power Transformers | Nos | 4 |
|  | End termination kit for 11kV, 1c x 1000sqmm cable | - For Terminating 11 kV Cables at all 11 kv incomer end - For Terminating 11 kV Cables at all Transformer end | Set | 36 |
|  | End Termination kit for 11kV, 3c x 300sqmm cable | For Terminating 11 kV Cables at 11 kV Capacitor Bank end and 11 kV Capacitor Panel end | Nos | 8 |
|  | 400 KVA Station Transformer |  | Nos | 1 |
|  | Fire Resistant Coating | - On all cable specified in “Grid S/S Scope of Supply” - Fire rating-4 hours | Lot | 1 |
|  | Cable Sealing System | For all cables entering and exiting the Proposed Substation Building | Lot | 1 |
|  | Cable Support Structure | Mounting Cable for Power Transformers, Switchgear etc | Lot | 1 |
|  | Clamps, Connectors & Accessories |  | Lot | 1 |
|  | Insulating Sleeves | For 33 kV and 11 kV side Transformer bus bars | Lot | 1 |
|  | Shrouds | For Bare Conductors | Lot | 1 |
|  | AC Distribution Board |  | Nos | 1 |
|  | DC Distribution Board |  | Nos | 1 |
|  | SMPS Battery Charger |  | Nos | 1 |
|  | 220 V Li Ion Battery Bank |  | Nos | 1 |
|  | Control Cables with proper ferruling and tagging along with glands and lugs | For items specified in “Grid S/S Scope of Supply” | Lot | 1 |
|  | LT Power Cable | For items specified in “Grid S/S Scope of Supply” | Lot | 1 |
|  | Insulated Floor Coating | For Switchgear Room, Battery Bank Room, ACDB, DCDB Room | Lot | 1 |
|  | Cable Tray including bends etc with 50% spare capacity in each | - For routing Power, LT and Control Cables - For items specified in “Grid S/S Scope of Supply” - 50% spare capacity in each is tray is required | Lot | 1 |
|  | Complete Grid Earthing | Earthing of all Grid Substation and items specified in “Grid S/S Scope of Supply” | Lot | 1 |
|  | Fire protection system | For items specified in “Grid S/S Scope of Supply” | Lot | 1 |
|  | Illumination and lighting system |  | Lot | 1 |
|  | Exhaust and Ventilation system |  | Lot | 1 |
|  | Lightning Protection | For complete Grid S/S | Lot | 1 |
|  | Conduits | For Lighting, Ceiling Fans, Power Sockets, Exhaust Fans, etc. | Lot | 1 |
|  | SF6 Gas Handling Kit |  | No | 1 |
|  | Material for Civil Works | As specified in Scope of Work | Lot | 1 |
|  | Motorized De watering Facility | For water seepage | Lot | 1 |
|  | RTU & Associated SCADA Works |  | Lot | 1 |
|  | Painting of Feeder names (SCADA code, Asset Code, etc) | As per Engineer Incharge Guidance | Lot | 1 |
|  | Licensed programming software and communication cord for offered numerical relays |  | No | 1 |
|  | Tools |  |  |  |
|  | Special Tools | Corresponding to Items specified in "Grid S/S Scope of Supply" for ease of Operation and Maintenance | Lot | 1 |
|  | High voltage Test Set |  | No | 1 |
|  | Insulation Resistance Kit |  | No | 1 |
|  | Earthing Rod for Discharging Purpose |  | No | 1 |
|  | Live Line Detector |  | No | 1 |
|  | Bosch Professional Tool Kit |  | No | 1 |
|  | Portable Flash Light |  | No | 1 |
|  | A-Type ladder (3 feet height) to be supplied.( For viewing and operating Relays) |  | No | 1 |
|  | Stepped trolley cum platform | To access Relays of Switchgears | No | 2 |
|  | Recommended & Mandatory Spares as per Specification of Supplied items |  | Lot | 1 |
|  | Drinking Water Cooler | Water Purification Technology shall be RO | No | 1 |
|  | 9 Meter SMC Expandable Ladder |  | No | 1 |
|  | SLD of Grid | Covered in Acrylic Sheet | No | 1 |
|  | Video surveillance system |  | Lot | 1 |
|  | Emergency Exit Floor Marking | For Proposed Building | Lot | 1 |
|  | Air Conditioning | For Control Room and RTU | Lot | 1 |

### GRID S/S SCOPE OF WORK

- Broad scope of work is specified below. Refer respective equipment/work specifications for detailed scope of work.

| S. No | Items | Remarks | Unit | Qty |
| --- | --- | --- | --- | --- |
|  | Erection, Testing and Commissioning of all items specified in “Scope of Supply” |  | Lot | 1 |
|  | Retrofitting Work of Differential Relay at both receiving and sending end | - Erection, testing and commissioning - Cut out of switchgears for Relay erection purpose - Control cable works | Lot | 1 |
|  | Soil Resistivity Test | For earthing Design | No | 1 |
|  | Training on O&M of 33 KV GIS | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Training on application, programming, testing and commissioning of Numerical Relays | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Training on commissioning, operations and maintenance of 11KV Switchgear | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Training on commissioning, operations and maintenance of NIFPS | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Dismantling of Existing Building and Shifting of RMU | - It also includes disconnection and reconnection of Cables - It also includes civil works if any | Lot | 1 |
|  | Civil Works | Refer Specification for Civil Works |  |  |
|  | Site survey, Soil testing, design and engineering |  | Lot | 1 |
|  | Substation Building | Building shall be G+1 storey. However, if it is not possible to accommodate the equipment on G+1 storeys due to space constraint at site, G+2 storey shall be constructed to accommodate the equipment | No | 1 |
|  | Cable cellar at ground floor |  | No | 1 |
|  | 11kV switchgear room at First Floor |  | No | 1 |
|  | 66/33kV GIS Room at First floor |  | No | 1 |
|  | EOT Crane for 66kV GIS Room | Capacity shall be based on heaviest package with appropriate safety margin. Minimum capacity shall be 5 tons | No | 1 |
|  | Control Room at First Floor | For housing CRP, ACDB, DCDB, RTU etc | No | 1 |
|  | Battery Room at First Floor |  | No | 1 |
|  | Maintenance Room at First Floor |  | No | 1 |
|  | Pantry at First floor |  | No | 1 |
|  | Washroom at First Floor |  | No | 1 |
|  | Two side entry and exit |  | Lot | 1 |
|  | Fire retardant windows and doors | Fire rating for 2 hours withstand | Lot | 1 |
|  | Motorized Shutter | For Entry and Exit of Switchgears | No | 1 |
|  | Table |  | No | 2 |
|  | Chair |  | No | 6 |
|  | MS Almirah |  | No | 3 |
|  | Water tank and booster pump |  | Lot | 1 |
|  | Yard Works |  |  |  |
|  | Foundation Works | For all equipment included in “Grid S/S Scope of supply” | Lot | 1 |
|  | Levelling for compete plot area |  | Lot | 1 |
|  | Boundary wall with Barbed Wire |  | Lot | 1 |
|  | Power Cable Trench | With 50% spare capacity for future use | Lot | 1 |
|  | Control Cable Trench | With 50% spare capacity for future use | Lot | 1 |
|  | Support Structure and appropriate clamping arrangement | For proper termination of all power and control cables | Lot | 1 |
|  | Chequered Plate for trenches |  | Lot | 1 |
|  | Motorized De-Watering system for trenches |  | Lot | 1 |
|  | Sump Pit | - Joining of all Power Transformer with Respective Soak Pit - Capacity shall be 20000 Liters - Motorized Dewatering/ De-oiling for Sump Pit | No | 1 |
|  | Soak Pit | For All Power Transformers | No | 2 |
|  | Fire Walls | For power transformers | Lot | 1 |
|  | Fencing | - For all outdoor equipment - Pre-galvanized MS Fencing with powder coating - Fencing shall be Anticut and anticlimb type | Lot | 1 |
|  | Main Gate | MS gate of size 6.5m | No | 2 |
|  | 6m Road | Between Gates, Substation Building, Power Transformers, Station Transformer, Auto Switched Capacitor Bank | Lot | 1 |
|  | Yard Development | For Complete outdoor Yard Area | Lot | 1 |
|  | Rain Water Harvesting |  | No | 1 |
|  | Guard Room |  | No | 1 |
|  | Drainage and Sewage System |  | Lot | 1 |

### GRID S/S SLD

### OUTGOING SCOPE OF SUPPLY

| S No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Cable 11 kV 3Cx300 sq mm | Meter | 5800 |
|  | Cable Indoor End Termination kit suitable for 11 kV 3Cx300 sq mm cable (Make-Raychem/3M/Yamuna Power Infrastructure) | No's | 15 |
|  | Cable straight through joint kit suitable for 11 kV 3Cx300 sq mm cable (Make-Raychem/3M/Yamuna Power Infrastructure) | No's | 19 |
|  | Motorized RMU (ABB make) along with FRTU, Battery Bank and Battery Charger Indoor - 1 Way | No's | 1 |
|  | Motorized RMU along with FRTU, Battery Bank and Battery Charger Outdoor - 3 Way | No's | 1 |
|  | Precast RCC (1:2:4) cable cover 600x300x50 mm | No's | 8217 |
|  | HDPE PIPE 180 MM DIA PN6 PE 80 | Meter | 2030 |
|  | HDPE Pipe Collar 180 mm | No's | 338 |
|  | RCC coffin for straight through Joint | No's | 19 |
|  | RCC Plate for straight through Joint | No's | 19 |
|  | Weather and acid resistant PVC warning tape of 150mm width 300 micron thick Yellow colour with desired Red/Black printing. | Meter | 4930 |
|  | Route indicating stone at every 50 meter circuit length and Joint indicating stones at every cable joint location | No's | 135 |
|  | Galvanized Channel, Angle, Beam and other Structural steel with hardwares for all structures including cable support Structure | MT | 1 |
|  | Fine Sand | Cubic meter | 532 |
|  | End Cap for Cable 11 KV AL 3X300 Sqmm XLPE | No's | 39 |
|  | HDPE cleat with hardware's suitable for 11 kV 3Cx300 sq mm cable | No's | 12 |
|  | Danger Plates | No's | 6 |
|  | Circuit Name Plate | No's | 6 |
|  | Cable Identitication Road Stud | No's | 1 |
|  | Aluminium Cable Identification tag with nylon string | No's | 193 |
|  | Safety barricading PVC tape | Meter | 1 |
|  | Safety barricading cone | No's | 1 |
|  | RFID based electronic buried type cable route marker for cable joints and turns having facility to feed the joint/turn related information | No's | 1 |
|  | Galvanized Nuts & Bolts | Kg | 1 |
|  | Coarse sand for PCC & RCC | Cubic meter | 1 |
|  | Burnt clay Brick - First class | No's | 1 |
|  | Cement Bags 50 kg | No's | 1 |
|  | Reinforcement steel bars | MT | 1 |
|  | Construction Aggregate | Cubic meter | 1 |
|  | Chemical earthing kit (3 Meter Cu Bonded Rod, Chemical, Polyplastic Pit cover | Lot | 1 |
|  | Cu bonded rod for mesh formation of earthing | Lot | 1 |
|  | Phase marking Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) | Lot | 1 |
|  | cable sheath repair 3M Scotch 2228 Rubber mastic Tape | Lot | 1 |
|  | Self-Fusing Silicone Rubber Electrical Tape 70 | Lot | 1 |
|  | Fire retardant coating for application on outgoing Power cables | Lot | 1 |

### OUTGOING SCOPE OF WORK

| S No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Surveying of cable Route, Detailed Site Plan & Profile using Ground penetration Radar System, Excavation of trial pits as per field requirement, preparation of route drawing with location of joint chambers position and finalizing the cable route in consultation with BSES Representative | Meter | 5800 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Ordinary Bituminous/C.C.Road (including dewatering if any) | Cubic meter | 734 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Dense Carpeted bituminous Road (including dewatering if any) | Cubic meter | 612 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Footpath/tile/Rajasthani Stone/Brick work (including dewatering if any) | Cubic meter | 612 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Hard Rocky Soil (including dewatering if any) | Cubic meter | 122 |
|  | Laying of XLPE cables in the excavated trench, as per BYPL Standards (Regarding Depth, Layer formation, etc). Cable rollers to be used during Laying. | Meter | 3770 |
|  | Laying of XLPE cable in HDPE/Hume/GI in excavated trench | Meter | 1160 |
|  | Laying of cable in trenchless ducts including laying of cable and HDPE pipe using HDD machine including laying of 200 mm dia HDPE pipe PN4 PE 80 Class | Meter | 870 |
|  | Continuous steel Barricading for all Excavated areas, till the work is completed. | Meter | 4930 |
|  | Fixing of Aluminum Cable identification tags with Nylon string at every 30 Mtrs cable length | No's | 193 |
|  | Installation of straight through joints for 11 kv 3Cx300 sq mm cables by jointing kit OEM authorized jointer | No's | 19 |
|  | Installation of End Termination kit for 11 kV 3Cx300 sq mm cable by jointing kit OEM authorized jointer | No's | 15 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Ordinary bituminous road/C.C. Road | No's | 5 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Dense carpeted bituminous road. | No's | 5 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Footpath/ tile/ Rajasthani Stone / Brick Works | No's | 5 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Hard Rocky Soil. | No's | 4 |
|  | Spreading of sand forming cushion and cover around the cable | Cubic meter | 532 |
|  | Disposal of debris/surplus malba including Loading / Unloading | Cubic meter | 586 |
|  | Digging of test pits of required size( not less than 1/2 Meter Wide at site for identification of cable route) | No's | 2 |
|  | Watch and ward of complete circuit till project handover | Lot | 1 |
|  | Installation of precast RCC Cable cover | No's | 8217 |
|  | Installation of Route and Joint indicating stone marked with "BYPL 11KV Cable Helpline No-91-11-399 99 808" | No's | 135 |
|  | Laying of PVC warning tape | Meter | 4930 |
|  | Fabrication and installation of galvanized channel, angel, Beam and other structural steel including nuts & bolts for all structures including cable support structure | MT | 1 |
|  | Partial discharge test on complete cable length at site | Lot | 1 |
|  | VLF High voltage test & Tan Delta test on complete cable length as per relevant IEC/IEEE | Lot | 1 |
|  | Installation, mounting and fixing of 11 kV 3Cx300 sq mm cable with termination on mounting structure/tower and fixing it with suitable HDPE cleats | No's | 12 |
|  | Fixing of danger plate on poles including fabrication of clamps etc | No's | 6 |
|  | Fixing of circuit Name plate including fabrication of clamps etc | No's | 6 |
|  | Installation of Cable identification road stud | No's | 1 |
|  | Submission of actual laid drawing of cable circuits including GPS coordinates of all joint in cables circuits | No's | 2 |
|  | Cable Phasing work, Cable Phase Sequence (R,Y,B) Marking, Cable 1&2 Marking, and final connection as per Phase Sequence. | No's | 4 |
|  | Masonry Brick work | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:1.5:3 (1 cement :1.5 coarse sand : 3 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:2:4 (1 cement :2 coarse sand : 4 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:4:8 (1 cement :4 coarse sand : 8 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Centering, shuttering including shuttering propping etc and removal of shuttering | Lot | 1 |
|  | Fabrication of reinforcement for RCC work including straightening, cutting, bending, placing in position and binding all complete thermo mechanically treated bars. | Lot | 1 |
|  | Installation of Brick as Cable Separator | No's | 1 |
|  | ETC of RFID Active Marker | No's | 1 |
|  | Installation of RCC Coffin for Cable Joint | No's | 19 |
|  | Installation of RCC Plate for Cable Joint | No's | 19 |
|  | Application of Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) on cable end termination kit | Lot | 1 |
|  | Application of 3M Scotch 2228 Rubber mastic Tape on cable straight through joint end sealing and for cable sheath repair | Lot | 1 |
|  | Application of Self-Fusing Silicone Rubber Electrical Tape 70 on cable end termination boot and lug | Lot | 1 |
|  | Application of fire retardant coating on outgoing Power cables in yard boundary and exposed areas | Lot | 1 |
|  | ETC of Motorized RMU (ABB make) along with FRTU, Battery Bank and Battery Charger Indoor - 1 Way | No's | 1 |
|  | ETC of Motorized RMU along with FRTU, Battery Bank and Battery Charger Outdoor - 3 Way | No's | 1 |
|  | ETC of Earthing Work | Lot | 1 |

## PACKAGE -2 - HARGOBIND ENCLAVE GRID S/S WITH INFEED AND OUTGOING

- Site detail, Scope of Supply and Scope of Work of Infeed, Grid S/S and Outgoing Feeder are given below

### INFEED SITE DETAIL

- DTL 220 kV Preet Vihar to BYPL Hargobind Enclave Grid

- 2 No's Circuits  of length 500 meter each therefore cable length of 2000 meter.

- Each circuit consists of two runs of cable.

### INFEED SCOPE OF SUPPLY

| S No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Cable 33 kV 3Cx400 sq mm | Meter | 2000 |
|  | Cable End Termination kit for GIS panel suitable for 33 kV 3Cx400 sq mm cable (Make- Raychem/3M) | No's | 8 |
|  | Cable straight through joint kit Suitable for 33 kV 3Cx400 sq mm cable(Make- Raychem/3M) | No's | 8 |
|  | Precast RCC (1:2:4) cable cover 600x550x50 mm (used where 4 cable runs in one trench) | No's | 1417 |
|  | HDPE PIPE 200 MM DIA PN4 PE 80 | Meter | 700 |
|  | HDPE Pipe Collar 200 mm | No's | 117 |
|  | Weather and acid resistant PVC warning tape of 150mm width 300 micron thick Yellow colour with desired Red/Black printing. | Meter | 850 |
|  | Route indicating stone at every 50 meter circuit length and Joint indicating stones at every cable joint location | No's | 18 |
|  | Galvanized Channel, Angle, Beam and other Structural steel with hardwares for all structures including cable support Structure | MT | 1 |
|  | Fine Sand | Cubic meter | 153 |
|  | End Cap for Cable 33 KV AL 3X400 Sqmm XLPE | No's | 20 |
|  | Optical Fiber cable 48F (1 Run with each circuit) | Meter | 1000 |
|  | Duct for Optical Fibre Cable (40mm) | Meter | 1000 |
|  | Collar for optical fiber cable duct | No's | 10 |
|  | Optical Fiber cable splice enclosure for jointing of optical fiber cable | No's | 2 |
|  | Fibre optic cable end termination distribution box | No's | 4 |
|  | Cable armour- earth link box without SVL | No's | 8 |
|  | HDPE cleat with hardware's suitable for 33 kV 3Cx400 sq mm cable | No's | 16 |
|  | Support insulators for mounting of cable on support structure | No's | 8 |
|  | Danger Plates | No's | 8 |
|  | Circuit Name Plate | No's | 8 |
|  | Anti Climbing device | No's | 4 |
|  | Cable Identitication Road Stud | No's | 1 |
|  | 50X6 Sq mm GI Earthing strip | MT | 1 |
|  | Aluminium Cable Identification tag with nylon string | No's | 67 |
|  | Safety barricading PVC tape | Meter | 1 |
|  | Safety barricading cone | No's | 1 |
|  | RFID based electronic buried type cable route marker for cable joints and turns having facility to feed the joint/turn related information | No's | 1 |
|  | Receiver unit for electronic cable route marker Cum cable route tracer suitable with offline as well as online cable route tracing functionality | No's | 1 |
|  | Coarse sand for PCC & RCC | Cubic meter | 1 |
|  | Burnt clay Brick - First class | No's | 1 |
|  | Cement Bags 50 kg | No's | 1 |
|  | Reinforcement steel bars | MT | 1 |
|  | Construction Aggregate | Cubic meter | 1 |
|  | Optical Fiber cable loop chamber for every 300 meter of cable run | No's | 3 |
|  | Phase marking Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) | Lot | 1 |
|  | cable sheath repair 3M Scotch 2228 Rubber mastic Tape | Lot | 1 |
|  | Self-Fusing Silicone Rubber Electrical Tape 70 | Lot | 1 |
|  | Fire retardant coating for application on Power cables and Optical fiber cable | Lot | 1 |

### INFEED SCOPE OF WORK

| S. No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Surveying of cable Route, Detailed Site Plan & Profile using Ground penetration Radar System, Excavation of trial pits as per field requirement, preparation of route drawing with location of joint chambers position and finalizing the cable route in consultation with BSES Representative | Meter | 500 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Ordinary Bituminous/C.C.Road (including dewatering if any) | Cubic meter | 185 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Dense Carpeted bituminous Road (including dewatering if any) | Cubic meter | 148 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Footpath/tile/Rajasthani Stone/Brick work (including dewatering if any) | Cubic meter | 148 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Hard Rocky Soil (including dewatering if any) | Cubic meter | 148 |
|  | Laying of XLPE cables in the excavated trench, as per BYPL Standards (Regarding Depth, Layer formation, etc). Cable rollers to be used during Laying. | Meter | 1300 |
|  | Laying of XLPE cable in HDPE pipe in excavated trench | Meter | 400 |
|  | Laying of cable in trenchless ducts including laying of cable and HDPE pipe using HDD machine including laying of 200 mm dia HDPE pipe PN4 PE 80 Class | Meter | 300 |
|  | Continuous steel Barricading for all Excavated areas, till the work is completed. | Lot | 1 |
|  | Fixing of Aluminum Cable identification tags with Nylon string at every 30 Mtrs cable length | No's | 67 |
|  | Installation of straight through joints for 33 kv 3Cx400 sq mm cables by jointing kit OEM authorized jointer | No's | 8 |
|  | Instalation of End Termination kit in 33 kV GIS suitable for 33 kV 3Cx400 sq mm cable by jointing kit OEM authorized jointer | No's | 8 |
|  | Digging of joint pit suitable for 33 cable joint box and covering the joint box with sand and providing protection for Ordinary bituminous road/C.C. Road | No's | 2 |
|  | Digging of joint pit suitable for 33 cable joint box and covering the joint box with sand and providing protection for Dense carpeted bituminous road. | No's | 2 |
|  | Digging of joint pit suitable for 33 cable joint box and covering the joint box with sand and providing protection for Footpath/ tile/ Rajasthani Stone / Brick Works | No's | 2 |
|  | Digging of joint pit suitable for 33 cable joint box and covering the joint box with sand and providing protection for Hard Rocky Soil. | No's | 2 |
|  | Spreading of sand forming cushion and cover around the cable | Cubic meter | 153 |
|  | Disposal of debris/surplus malba including Loading / Unloading | Cubic meter | 168 |
|  | Digging of test pits of required size( not less than 1/2 Meter Wide at site for identification of cable route) | No's | 2 |
|  | Watch and ward of complete circuit till project handover | Lot | 1 |
|  | Installation of precast RCC Cable cover | No's | 1417 |
|  | Installation of Route and Joint indicating stone marked with "BYPL 33 KV Cable Helpline No-91-11-399 99 808" | No's | 18 |
|  | Laying of PVC warning tape | Meter | 850 |
|  | Fabrication and installation of galvanized channel, angel, Beam and other structural steel including nuts & bolts for all structures including cable support structure | MT | 1 |
|  | Laying of optical fiber cable in 40 mm duct including blowing and pulling | Meter | 1000 |
|  | Installation of OFC cable splice enclosure | No's | 2 |
|  | Testing of optical fiber cable after installation | Lot | 1 |
|  | Partial discharge test on complete cable length at site | Lot | 1 |
|  | VLF High voltage test & Tan Delta test on complete cable length as per relevant IEC/IEEE | Lot | 1 |
|  | Installation of Fiber optic cable distribution box for termination of fiber optic cable | No's | 4 |
|  | Installation of cable armour- earth link box without SVL including cable earthing/armour connection with grid earthing | No's | 8 |
|  | Installation, mounting and fixing of 33 kV 3Cx400 sq mm cable with termination on mounting structure/tower and fixing it with suitable HDPE cleats | No's | 16 |
|  | Installation of support insulators on cable mounting structure with misc. hardware's. | No's | 8 |
|  | Fixing of danger plate on poles including fabrication of clamps etc | No's | 8 |
|  | Fixing of circuit Name plate including fabrication of clamps etc | No's | 8 |
|  | Fixing of anti climbing device on cables mounting structures including fabrication of clamps etc | No's | 4 |
|  | Installation of Cable identification road stud | No's | 1 |
|  | Transportation of empty 33 kV cable drums from site to BSES store | No's | 10 |
|  | Laying of GI earth connecting strip of 50x6 sq mm size including required welding, painting on joints etc | MT | 1 |
|  | Submission of actual laid drawing of cable circuits including GPS coordinates of all joint in cables circuits | Lot | 1 |
|  | Cable Phasing work, Cable Phase Sequence (R,Y,B) Marking, Cable 1&2 Marking, and final connection as per Phase Sequence. | Lot | 1 |
|  | Masonry Brick work | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:1.5:3 (1 cement :1.5 coarse sand : 3 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:2:4 (1 cement :2 coarse sand : 4 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:4:8 (1 cement :4 coarse sand : 8 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Centering, shuttering including shuttering propping etc and removal of shuttering | Lot | 1 |
|  | Fabrication of reinforcement for RCC work including straightening, cutting, bending, placing in position and binding all complete thermo mechanically treated bars. | Lot | 1 |
|  | Installation of Brick as Cable Separator | No's | 1 |
|  | Installation of Optical Fiber cable loop chamber | No's | 3 |
|  | ETC of RFID Marker | No's | 1 |
|  | Application of Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) on cable end termination kit | Lot | 1 |
|  | Application of 3M Scotch 2228 Rubber mastic Tape on cable straight through joint end sealing and for cable sheath repair | Lot | 1 |
|  | Application of Self-Fusing Silicone Rubber Electrical Tape 70 on cable end termination boot and lug | Lot | 1 |
|  | Application of fire retardant coating on Infeed Power cables and Optical fibre cable in yard boundary and exposed areas | Lot | 1 |
|  | Design, Engineering, construction of bridge over Shahdara Drain for crossing of 10 No's 11 kV 3Cx300 sq mm and 10 No's 3 kV 3Cx400 sq mm cable as per tender specification | Lot | 1 |

### GRID S/S DETAIL

- 33 kV /11 kV Hargobind Enclave Grid S/S is situated Near 220 kV DTL Preet Vihar Grid S/S behind Shanti Mukand Hospital, Anand Vihar , Delhi 110092.

### GRID S/S SCOPE OF SUPPLY

| S No. | Items | Remarks | UOM | Qty |
| --- | --- | --- | --- | --- |
|  | 33 kV GIS with Double Bus Bar Arrangement as per SLD Attached | - Arrangement also includes Bus Riser Panel wherever applicable - Line Differential Protection Relay shall be supplied as Relay 1 (Main protection) of incomer feeder for Both Receiving and Sending End. |  |  |
|  | Incomer Feeder with Line PT |  | Nos | 3 |
|  | Transformer Feeder |  | Nos | 2 |
|  | Bus Coupler |  | Nos | 1 |
|  | Bus PT |  | Nos | 2 |
|  | 25 MVA, 33 kV/11 kV Power Transformer (Including Marshalling Box and NIFPS) |  | Nos | 2 |
|  | 11 kV Switchboard | Arrangement also includes Bus Riser Panel wherever applicable |  |  |
|  | Incoming panel (with Line PT) |  | Nos | 2 |
|  | Bus Coupler Panel(Having Provision for termination of 3 x 1c x 1000sqmm cable per phase) |  | Nos | 1 |
|  | Bus PT |  | Nos | 1 |
|  | Capacitor Panel |  | Nos | 2 |
|  | Outgoing Panel |  | Nos | 16 |
|  | Station Transformer Panel |  | Nos | 1 |
|  | Earthing Truck for Bus bar Side Earthing |  | Nos | 2 |
|  | Earthing Truck for Cable bar Side Earthing |  | Nos | 2 |
|  | 11 kV Auto Switched Capacitor Bank |  | Nos | 2 |
|  | 33 kV 3CX400 XLPE insulated, stranded aluminum conductor, PVC outer sheath Power cable | For connecting all power transformer from 33 kV Trafo panel | Lot | 1 |
|  | 11 kV 1CX1000 sqmm XLPE insulated, stranded Aluminium conductor, PVC outer sheath cable | All Power transformer to 11 kV incoming Panel | Lot | 1 |
|  | 11 kV 3CX300 sqmm XLPE insulated, stranded aluminum conductor, PVC outer sheath Power cable | For 11 kV Capacitor Bank | Lot | 1 |
|  | GIS termination kit for 33kV, 3c x 400sqmm cable | For termination at 33kV GIS | Nos | 2 |
|  | End Termination kit for 33kV, 3CX400 sqmm Cable | For connecting cable to the bushing of power Transformers | Nos | 4 |
|  | End termination kit for 11kV, 1c x 1000sqmm cable | - For Terminating 11 kV Cables at all 11 kv incomer end - For Terminating 11 kV Cables at all Transformer end | Set | 36 |
|  | End Termination kit for 11kV, 3c x 300sqmm cable | For Terminating 11 kV Cables at 11 kV Capacitor Bank end and 11 kV Capacitor Panel end | Nos | 8 |
|  | 400 KVA Station Transformer |  | Nos | 1 |
|  | Fire Resistant Coating | - On all cable specified in “Grid S/S Scope of Supply” - Fire rating-4 hours | Lot | 1 |
|  | Cable Sealing System | For all cables entering and exiting the Proposed Substation Building | Lot | 1 |
|  | Cable Support Structure | Mounting Cable for Power Transformers, Switchgear etc | Lot | 1 |
|  | Clamps, Connectors & Accessories |  | Lot | 1 |
|  | Insulating Sleeves | For 33 kV and 11 kV side Transformer bus bars | Lot | 1 |
|  | Shrouds | For Bare Conductors | Lot | 1 |
|  | AC Distribution Board |  | Nos | 1 |
|  | DC Distribution Board |  | Nos | 1 |
|  | SMPS Battery Charger |  | Nos | 1 |
|  | 220 V Li Ion Battery Bank |  | Nos | 1 |
|  | Control Cables with proper ferruling and tagging along with glands and lugs | For items specified in “Grid S/S Scope of Supply” | Lot | 1 |
|  | LT Power Cable | For items specified in “Grid S/S Scope of supply” | Lot | 1 |
|  | Insulated Floor Coating | For Switchgear Room, Battery Bank Room, ACDB, DCDB Room | Lot | 1 |
|  | Cable Tray including bends etc with 50% spare capacity in each | - For routing Power, LT and Control Cables - For items specified in “Grid S/S Scope of Supply” - 50% spare capacity in each is tray is required | Lot | 1 |
|  | Complete Grid Earthing | Earthing of all Grid Substation and items specified in “Grid S/S Scope of Supply” | Lot | 1 |
|  | Fire protection system | For items specified in “Grid S/S Scope of Supply” | Lot | 1 |
|  | Illumination and lighting system |  | Lot | 1 |
|  | Exhaust and Ventilation system |  | Lot | 1 |
|  | Lightning Protection | For complete Grid S/S | Lot | 1 |
|  | Conduits | For Lighting, Ceiling Fans, Power Sockets, Exhaust Fans, etc. | Lot | 1 |
|  | SF6 Gas Handling Kit |  | No | 1 |
|  | Material for Civil Works | As specified in Grid S/S Scope of Work | Lot | 1 |
|  | Motorized De watering Facility | For water seepage | Lot | 1 |
|  | RTU & Associated SCADA Works |  | Lot | 1 |
|  | Painting of Feeder names (SCADA code, Asset Code, etc) | As per Engineer Incharge Guidance | Lot | 1 |
|  | Licensed programming software and communication cord for offered numerical relays |  | No | 1 |
|  | Tools |  |  |  |
|  | Special Tools | Corresponding to Items specified in "Grid S/S Scope of Supply" for ease of Operation and Maintenance | Lot | 1 |
|  | High voltage Test Set |  | No | 1 |
|  | Insulation Resistance Kit |  | No | 1 |
|  | Earthing Rod for Discharging Purpose |  | No | 1 |
|  | Live Line Detector |  | No | 1 |
|  | Bosch Professional Tool Kit |  | No | 1 |
|  | Portable Flash Light |  | No | 1 |
|  | A-Type ladder (3 feet height) to be supplied.( For viewing and operating Relays) |  | No | 1 |
|  | Stepped trolley cum platform | To access Relays of Switchgears | No | 2 |
|  | Recommended & Mandatory Spares as per Specification of Supplied items |  | Lot | 1 |
|  | Drinking Water Cooler | Water Purification Technology shall be RO | No | 1 |
|  | 9 Meter SMC Expandable Ladder |  | No | 1 |
|  | SLD of Grid | Covered in Acrylic Sheet | No | 1 |
|  | Video surveillance system |  | Lot | 1 |
|  | Emergency Exit Floor Marking | For Proposed Building | Lot | 1 |
|  | Air Conditioning | For Control Room and RTU | Lot | 1 |

### GRID S/S SCOPE OF WORK

- Broad scope of work is specified below. Refer respective equipment/work specifications for detailed scope of work.

| S. No | Items | Remarks | Unit | Qty |
| --- | --- | --- | --- | --- |
|  | Erection, Testing and Commissioning of all items specified in “Grid S/S Scope of Supply” |  | Lot | 1 |
|  | Retrofitting Work of Differential Relay at both receiving and sending end | - Erection, testing and commissioning - Cut out of switchgears for Relay erection purpose - Control cable works | Lot | 1 |
|  | Soil Resistivity Test | For earthing Design | No | 1 |
|  | Training on O&M of 33 KV GIS | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Training on application, programming, testing and commissioning of Numerical Relays | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Training on commissioning, operations and maintenance of 11KV Switchgear | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Training on commissioning, operations and maintenance of NIFPS | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Dismantling of Existing Building |  | Lot | 1 |
|  | Civil Works | Refer Specification for Civil Works |  |  |
|  | Site survey, Soil testing, design and engineering |  | Lot | 1 |
|  | Substation Building | Building shall be G+1 storey. However, if it is not possible to accommodate the equipment on G+1 storeys due to space constraint at site, G+2 storey shall be constructed to accommodate the equipment | No | 1 |
|  | Cable cellar at ground floor |  | No | 1 |
|  | 11kV switchgear room at First Floor |  | No | 1 |
|  | 66/33kV GIS Room at First floor |  | No | 1 |
|  | EOT Crane for 66kV GIS Room | Capacity shall be based on heaviest package with appropriate safety margin. Minimum capacity shall be 5 tons | No | 1 |
|  | Control Room at First Floor | For housing CRP, ACDB, DCDB, RTU etc | No | 1 |
|  | Battery Room at First Floor |  | No | 1 |
|  | Maintenance Room at First Floor |  | No | 1 |
|  | Pantry at First floor |  | No | 1 |
|  | Washroom at First Floor |  | No | 1 |
|  | Two side entry and exit |  | Lot | 1 |
|  | Fire retardant windows and doors | Fire rating for 2 hours withstand | Lot | 1 |
|  | Motorized Shutter | For Entry and Exit of Switchgears | No | 1 |
|  | Table |  | No | 2 |
|  | Chair |  | No | 6 |
|  | MS Almirah |  | No | 3 |
|  | Water tank and booster pump |  | Lot | 1 |
|  | Yard Works |  |  |  |
|  | Foundation Works | For all equipment included in “Grid S/S Scope of supply” | Lot | 1 |
|  | Levelling for compete plot area |  | Lot | 1 |
|  | Boundary wall with Barbed Wire |  | Lot | 1 |
|  | Power Cable Trench | With 50% spare capacity for future use | Lot | 1 |
|  | Control Cable Trench | With 50% spare capacity for future use | Lot | 1 |
|  | Support Structure and appropriate clamping arrangement | For proper termination of all power and control cables | Lot | 1 |
|  | Chequered Plate for trenches |  | Lot | 1 |
|  | Motorized De-Watering system for trenches |  | Lot | 1 |
|  | Sump Pit | - Joining of all Power Transformer with Respective Soak Pit - Capacity -20000 Liters - Motorized Dewatering/ De-oiling for Sump Pit | No | 1 |
|  | Soak Pit | For All Power Transformers | No | 2 |
|  | Fire Walls | For power transformers | Lot | 1 |
|  | Fencing | - For all outdoor equipment - Pre-galvanized MS Fencing with powder coating - Fencing shall be Anticut and anticlimb type | Lot | 1 |
|  | Main Gate | MS gate of size 6.5m | No | 2 |
|  | 6m Road | Between Gates, Substation Building, Power Transformers, Station Transformer, Auto Switched Capacitor Bank | Lot | 1 |
|  | Yard Development | For Complete outdoor Yard Area | Lot | 1 |
|  | Rain Water Harvesting |  | No | 1 |
|  | Guard Room |  | No | 1 |
|  | Drainage and Sewage System |  | Lot | 1 |

### GRID S/S SLD

### OUTGOING SCOPE OF SUPPLY

| S. No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Cable 11 kV 3Cx300 sq mm | Meter | 10050 |
|  | Cable Indoor End Termination kit suitable for 11 kV 3Cx300 sq mm cable (Make-Raychem/3M/Yamuna Power Infrastructure) | No's | 27 |
|  | Cable straight through joint kit suitable for 11 kV 3Cx300 sq mm cable (Make-Raychem/3M/Yamuna Power Infrastructure) | No's | 34 |
|  | Motorized RMU along with FRTU, Battery Bank and Battery Charger Indoor - 3 Way | No's | 4 |
|  | Motorized RMU along with FRTU, Battery Bank and Battery Charger Outdoor - 3 Way | No's | 1 |
|  | Motorized RMU (AREVA make) along with FRTU, Battery Bank and Battery Charger Outdoor - 1 Way | No's | 1 |
|  | Precast RCC (1:2:4) cable cover 600x300x50 mm | No's | 14238 |
|  | HDPE PIPE 180 MM DIA PN6 PE 80 | Meter | 3518 |
|  | HDPE Pipe Collar 180 mm | No's | 586 |
|  | RCC coffin for straight through Joint | No's | 34 |
|  | RCC Plate for straight through Joint | No's | 34 |
|  | Weather and acid resistant PVC warning tape of 150mm width 300 micron thick Yellow colour with desired Red/Black printing. | Meter | 8543 |
|  | Route indicating stone at every 50 meter circuit length and Joint indicating stones at every cable joint location | No's | 235 |
|  | Galvanized Channel, Angle, Beam and other Structural steel with hardwares for all structures including cable support Structure | MT | 1 |
|  | Fine Sand | Cubic meter | 923 |
|  | End Cap for Cable 11 KV AL 3X300 Sqmm XLPE | No's | 67 |
|  | HDPE cleat with hardware's suitable for 11 kV 3Cx300 sq mm cable | No's | 12 |
|  | Danger Plates | No's | 6 |
|  | Circuit Name Plate | No's | 6 |
|  | Cable Identitication Road Stud | No's | 1 |
|  | Aluminium Cable Identification tag with nylon string | No's | 335 |
|  | Safety barricading PVC tape | Meter | 1 |
|  | Safety barricading cone | No's | 1 |
|  | RFID based electronic buried type cable route marker for cable joints and turns having facility to feed the joint/turn related information | No's | 1 |
|  | Galvanized Nuts & Bolts | Kg | 1 |
|  | Coarse sand for PCC & RCC | Cubic meter | 1 |
|  | Burnt clay Brick - First class | No's | 1 |
|  | Cement Bags 50 kg | No's | 1 |
|  | Reinforcement steel bars | MT | 1 |
|  | Construction Aggregate | Cubic meter | 1 |
|  | Chemical earthing kit (3 Meter Cu Bonded Rod, Chemical, Polyplastic Pit cover | Lot | 1 |
|  | Cu bonded rod for mesh formation of earthing | Lot | 1 |
|  | Phase marking Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) | Lot | 1 |
|  | cable sheath repair 3M Scotch 2228 Rubber mastic Tape | Lot | 1 |
|  | Self-Fusing Silicone Rubber Electrical Tape 70 | Lot | 1 |
|  | Fire retardant coating for application on outgoing Power cables | Lot | 1 |

### OUTGOING SCOPE OF WORK

| S. No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Surveying of cable Route, Detailed Site Plan & Profile using Ground penetration Radar System, Excavation of trial pits as per field requirement, preparation of route drawing with location of joint chambers position and finalizing the cable route in consultation with BSES Representative | Meter | 10050 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Ordinary Bituminous/C.C.Road (including dewatering if any) | Cubic meter | 1060 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Dense Carpeted bituminous Road (including dewatering if any) | Cubic meter | 848 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Footpath/tile/Rajasthani Stone/Brick work (including dewatering if any) | Cubic meter | 848 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Hard Rocky Soil (including dewatering if any) | Cubic meter | 848 |
|  | Laying of XLPE cables in the excavated trench, as per BYPL Standards (Regarding Depth, Layer formation, etc). Cable rollers to be used during Laying. | Meter | 6533 |
|  | Laying of XLPE cable in HDPE/Hume/GI in excavated trench | Meter | 2010 |
|  | Laying of cable in trenchless ducts including laying of cable and HDPE pipe using HDD machine including laying of 200 mm dia HDPE pipe PN4 PE 80 Class | Meter | 1508 |
|  | Continuous steel Barricading for all Excavated areas, till the work is completed. | Meter | 8543 |
|  | Fixing of Aluminum Cable identification tags with Nylon string at every 30 Mtrs cable length | No's | 335 |
|  | Installation of straight through joints for 11 kv 3Cx300 sq mm cables by jointing kit OEM authorized jointer | No's | 34 |
|  | Instalation of End Termination kit for 11 kV 3Cx300 sq mm cable by jointing kit OEM authorized jointer | No's | 27 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Ordinary bituminous road/C.C. Road | No's | 8 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Dense carpeted bituminous road. | No's | 8 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Footpath/ tile/ Rajasthani Stone / Brick Works | No's | 8 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Hard Rocky Soil. | No's | 10 |
|  | Spreading of sand forming cushion and cover around the cable | Cubic meter | 923 |
|  | Disposal of debris/surplus malba including Loading / Unloading | Cubic meter | 1015 |
|  | Digging of test pits of required size( not less than 1/2 Meter Wide at site for identification of cable route) | No's | 2 |
|  | Watch and ward of complete circuit till project handover | Lot | 1 |
|  | Installation of precast RCC Cable cover | No's | 14238 |
|  | Installation of Route and Joint indicating stone marked with "BYPL 11 KV Cable Helpline No-91-11-399 99 808" | No's | 235 |
|  | Laying of PVC warning tape | Meter | 8543 |
|  | Fabrication and installation of galvanized channel, angel, Beam and other structural steel including nuts & bolts for all structures including cable support structure | MT | 1 |
|  | Partial discharge test on complete cable length at site | Lot | 1 |
|  | VLF High voltage test & Tan Delta test on complete cable length as per relevant IEC/IEEE | Lot | 1 |
|  | Installation, mounting and fixing of 11 kV 3Cx300 sq mm cable with termination on mounting structure/tower and fixing it with suitable HDPE cleats | No's | 12 |
|  | Fixing of danger plate on poles including fabrication of clamps etc | No's | 6 |
|  | Fixing of circuit Name plate including fabrication of clamps etc | No's | 6 |
|  | Installation of Cable identification road stud | No's | 1 |
|  | Submission of actual laid drawing of cable circuits including GPS coordinates of all joint in cables circuits | No's | 2 |
|  | Cable Phasing work, Cable Phase Sequence (R,Y,B) Marking, Cable 1&2 Marking, and final connection as per Phase Sequence. | No's | 4 |
|  | Masonry Brick work | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:1.5:3 (1 cement :1.5 coarse sand : 3 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:2:4 (1 cement :2 coarse sand : 4 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:4:8 (1 cement :4 coarse sand : 8 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Centering, shuttering including shuttering propping etc and removal of shuttering | Lot | 1 |
|  | Fabrication of reinforcement for RCC work including straightening, cutting, bending, placing in position and binding all complete thermo mechanically treated bars. | Lot | 1 |
|  | Installation of Brick as Cable Separator | No's | 1 |
|  | ETC of RFID Active Marker | No's | 1 |
|  | Installation of RCC Coffin for Cable Joint | No's | 34 |
|  | Installation of RCC Plate for Cable Joint | No's | 34 |
|  | Application of Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) on cable end termination kit | Lot | 1 |
|  | Application of 3M Scotch 2228 Rubber mastic Tape on cable straight through joint end sealing and for cable sheath repair | Lot | 1 |
|  | Application of Self-Fusing Silicone Rubber Electrical Tape 70 on cable end termination boot and lug | Lot | 1 |
|  | Application of fire retardant coating on outgoing Power cables in yard boundary and exposed areas | Lot | 1 |
|  | ETC of Motorized RMU along with FRTU, Battery Bank and Battery Charger Indoor - 3 Way | No's | 4 |
|  | ETC of Motorized RMU along with FRTU, Battery Bank and Battery Charger Outdoor - 3 Way | No's | 1 |
|  | ETC of Motorized RMU (AREVA make) along with FRTU, Battery Bank and Battery Charger Outdoor - 1 Way | No's | 1 |
|  | ETC of Earthing Work | Lot | 1 |

## PACKAGE-3 - MANDOLI JAIL COMPLEX GRID S/S WITH INFEED AND OUTGOING

- Site detail, Scope of Supply and Scope of Work of Infeed, Grid S/S and Outgoing Feeder are given below

### INFEED SITE DETAIL

- DTL 400 kV Harsh Vihar to BYPL Mandoli Jail Complex Grid

- 2 No's Circuits of length 5000 meter each therefore cable length of 20000 meter.

- Each circuit consists of two runs of cable.

### INFEED SCOPE OF SUPPLY

| S. No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Cable 66 kV 3Cx300 sq mm | Meter | 20000 |
|  | Cable End Termination kit for GIS panel suitable for 66 kV 3Cx300 sq mm cable (Make- Raychem/3M) | No's | 8 |
|  | Cable straight through joint kit Suitable for 66 kV 3Cx300 sq mm cable(Make- Raychem/3M) | No's | 100 |
|  | Precast RCC (1:2:4) cable cover 600x550x50 mm (used where 4 cable runs in one trench) | No's | 14167 |
|  | HDPE PIPE 200 MM DIA PN4 PE 80 | Meter | 7000 |
|  | HDPE Pipe Collar 200 mm | No's | 1167 |
|  | Weather and acid resistant PVC warning tape of 150mm width 300 micron thick Yellow colour with desired Red/Black printing. | Meter | 17000 |
|  | Route indicating stone at every 50 meter circuit length and Joint indicating stones at every cable joint location | No's | 200 |
|  | Galvanized Channel, Angle, Beam and other Structural steel with hardwares for all structures including cable support Structure | MT | 1 |
|  | Fine Sand | Cubic meter | 1530 |
|  | End Cap for Cable 66 KV AL 3X300 Sqmm XLPE | No's | 200 |
|  | Optical Fiber cable 48F (1 Run with each circuit) | Meter | 10000 |
|  | Duct for Optical Fibre Cable (40mm) | Meter | 10000 |
|  | Collar for optical fiber cable duct | No's | 100 |
|  | Optical Fiber cable splice enclosure for jointing of optical fiber cable | No's | 20 |
|  | Fibre optic cable end termination distribution box | No's | 4 |
|  | Cable armour- earth link box without SVL | No's | 8 |
|  | HDPE cleat with hardware's suitable for 66 kV 3Cx300 sq mm cable | No's | 16 |
|  | Support insulators for mounting of cable on support structure | No's | 8 |
|  | Danger Plates | No's | 8 |
|  | Circuit Name Plate | No's | 8 |
|  | Anti Climbing device | No's | 4 |
|  | Cable Identitication Road Stud | No's | 1 |
|  | 50X6 Sq mm GI Earthing strip | MT | 1 |
|  | Aluminium Cable Identification tag with nylon string | No's | 667 |
|  | Safety barricading PVC tape | Meter | 1 |
|  | Safety barricading cone | No's | 1 |
|  | RFID based electronic buried type cable route marker for cable joints and turns having facility to feed the joint/turn related information | No's | 1 |
|  | Receiver unit for electronic cable route marker cum cable route tracer suitable with offline as well as online cable route tracing functionality | No's | 1 |
|  | Coarse sand for PCC & RCC | Cubic meter | 1 |
|  | Burnt clay Brick - First class | No's | 1 |
|  | Cement Bags 50 kg | No's | 1 |
|  | Reinforcement steel bars | MT | 1 |
|  | Construction Aggregate | Cubic meter | 1 |
|  | Optical Fiber cable loop chamber for every 300 meter of cable run | No's | 67 |
|  | Phase marking Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) | Lot | 1 |
|  | cable sheath repair 3M Scotch 2228 Rubber mastic Tape | Lot | 1 |
|  | Self-Fusing Silicone Rubber Electrical Tape 70 | Lot | 1 |
|  | Fire retardant coating for application on Power cables and Optical fiber cable | Lot | 1 |

### INFEED SCOPE OF WORK

| S. No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Surveying of cable Route, Detailed Site Plan & Profile using Ground penetration Radar System, Excavation of trial pits as per field requirement, preparation of route drawing with location of joint chambers position and finalizing the cable route in consultation with BSES Representative | Meter | 5000 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Ordinary Bituminous/C.C.Road (including dewatering if any) | Cubic meter | 2108 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Dense Carpeted bituminous Road (including dewatering if any) | Cubic meter | 1686 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Footpath/tile/Rajasthani Stone/Brick work (including dewatering if any) | Cubic meter | 1686 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Hard Rocky Soil (including dewatering if any) | Cubic meter | 1686 |
|  | Laying of XLPE cables in the excavated trench, as per BYPL Standards (Regarding Depth, Layer formation, etc). Cable rollers to be used during Laying. | Meter | 13000 |
|  | Laying of XLPE cable in HDPE Pipe in excavated trench | Meter | 4000 |
|  | Laying of cable in trenchless ducts including laying of cable and HDPE pipe using HDD machine including laying of 200 mm dia HDPE pipe PN4 PE 80 Class | Meter | 3000 |
|  | Continuous steel Barricading for all Excavated areas, till the work is completed. | Lot | 1 |
|  | Fixing of Aluminum Cable identification tags with Nylon string at every 30 Mtrs cable length | No's | 667 |
|  | Installation of straight through joints for 66 kv 3Cx300 sq mm cables by jointing kit OEM authorized jointer | No's | 100 |
|  | Installation of End Termination kit in 66 kV GIS suitable for 66 kV 3Cx300 sq mm cable by jointing kit OEM authorized jointer | No's | 8 |
|  | Digging of joint pit suitable for 66 cable joint box and covering the joint box with sand and providing protection for Ordinary bituminous road/C.C. Road | No's | 25 |
|  | Digging of joint pit suitable for 66 cable joint box and covering the joint box with sand and providing protection for Dense carpeted bituminous road. | No's | 25 |
|  | Digging of joint pit suitable for 66 cable joint box and covering the joint box with sand and providing protection for Footpath/ tile/ Rajasthani Stone / Brick Works | No's | 25 |
|  | Digging of joint pit suitable for 66 cable joint box and covering the joint box with sand and providing protection for Hard Rocky Soil. | No's | 25 |
|  | Spreading of sand forming cushion and cover around the cable | Cubic meter | 1530 |
|  | Disposal of debris/surplus malba including Loading / Unloading | Cubic meter | 1683 |
|  | Digging of test pits of required size( not less than 1/2 Meter Wide at site for identification of cable route) | No's | 2 |
|  | Watch and ward of complete circuit till project handover | Lot | 1 |
|  | Installation of precast RCC Cable cover | No's | 14167 |
|  | Installation of Route and Joint indicating stone marked with "BYPL 66 KV Cable Helpline No-91-11-399 99 808" | No's | 200 |
|  | Laying of PVC warning tape | Meter | 17000 |
|  | Fabrication and installation of galvanized channel, angel, Beam and other structural steel including nuts & bolts for all structures including cable support structure | MT | 1 |
|  | Laying of optical fiber cable in 40 mm duct including blowing and pulling | Meter | 10000 |
|  | Installation of OFC cable splice enclosure | No's | 20 |
|  | Testing of optical fiber cable after installation | Lot | 1 |
|  | Partial discharge test on complete cable length at site | Lot | 1 |
|  | VLF High voltage test & Tan Delta test on complete cable length as per relevant IEC/IEEE | Lot | 1 |
|  | Installation of Fiber optic cable distribution box for termination of fiber optic cable | No's | 4 |
|  | Installation of cable armour- earth link box without SVL including cable earthing/armour connection with grid earthing | No's | 8 |
|  | Installation, mounting and fixing of 66 kV 3Cx300 sq mm cable with termination on mounting structure/tower and fixing it with suitable HDPE cleats | No's | 16 |
|  | Installation of support insulators on cable mounting structure with misc. hardware's. | No's | 8 |
|  | Fixing of danger plate on poles including fabrication of clamps etc | No's | 8 |
|  | Fixing of circuit Name plate including fabrication of clamps etc | No's | 8 |
|  | Fixing of anti climbing device on cables mounting structures including fabrication of clamps etc | No's | 4 |
|  | Installation of Cable identification road stud | No's | 1 |
|  | Transportation of empty 66 kV cable drums from site to BSES store | No's | 100 |
|  | Laying of GI earth connecting strip of 50x6 sq mm size including required welding, painting on joints etc | MT | 1 |
|  | Submission of actual laid drawing of cable circuits including GPS coordinates of all joint in cables circuits | Lot | 1 |
|  | Cable Phasing work, Cable Phase Sequence (R,Y,B) Marking, Cable 1&2 Marking, and final connection as per Phase Sequence. | Lot | 1 |
|  | Masonry Brick work | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:1.5:3 (1 cement :1.5 coarse sand : 3 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:2:4 (1 cement :2 coarse sand : 4 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:4:8 (1 cement :4 coarse sand : 8 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Centering, shuttering including shuttering propping etc and removal of shuttering | Lot | 1 |
|  | Fabrication of reinforcement for RCC work including straightening, cutting, bending, placing in position and binding all complete thermo mechanically treated bars. | Lot | 1 |
|  | Installation of Brick as Cable Separator | No's | 1 |
|  | Installation of Optical Fiber cable loop chamber | No's | 67 |
|  | ETC of RFID marker | No's | 1 |
|  | Application of Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) on cable end termination kit | Lot | 1 |
|  | Application of 3M Scotch 2228 Rubber mastic Tape on cable straight through joint end sealing and for cable sheath repair | Lot | 1 |
|  | Application of Self-Fusing Silicone Rubber Electrical Tape 70 on cable end termination boot and lug | Lot | 1 |
|  | Application of fire retardant coating on Infeed Power cables and Optical fibre cable in yard boundary and exposed areas | Lot | 1 |

### GRID S/S DETAIL

- 66 kV /11 kV Mandoli Jail Complex is located near Mangal Pandey Marg, Harsh Vihar, Mandoli, New Delhi, Delhi 110093.

### GRID S/S SCOPE OF SUPPLY

| S No. | Items | Remarks | UOM | Qty |
| --- | --- | --- | --- | --- |
|  | 66 kV GIS with Double Bus Bar Arrangement as per SLD Attached | - Arrangement also includes Bus Riser Panel wherever applicable - It also Includes LCC and CRP panel for associated Bay - Line Differential Protection Relay shall be supplied as Relay 1 (Main protection) of incomer feeder for Both Receiving and Sending End. |  |  |
|  | Incomer Feeder with Line PT |  | Nos | 4 |
|  | Transformer Feeder |  | Nos | 2 |
|  | Bus Coupler |  | Nos | 1 |
|  | Bus PT |  | Nos | 2 |
|  | Control And Relay Panel |  |  |  |
|  | Incomer Feeder |  | Nos | 4 |
|  | Transformer Feeder |  | Nos | 2 |
|  | Bus Coupler |  | Nos | 1 |
|  | 25 MVA, 66 kV/11 kV Power Transformer (Including Marshalling Box and NIFPS) |  | Nos | 2 |
|  | 11 kV Switchboard | Arrangement also includes Bus Riser Panel wherever applicable |  |  |
|  | Incoming panel (with Line PT) |  | Nos | 2 |
|  | Bus Coupler Panel |  | Nos | 1 |
|  | Bus PT |  | Nos | 1 |
|  | Capacitor Panel |  | Nos | 2 |
|  | Outgoing Panel |  | Nos | 16 |
|  | Station Transformer Panel |  | Nos | 1 |
|  | Earthing truck for bus-bar side earthing |  | Nos | 2 |
|  | Earthing truck for cable side earthing |  | Nos | 2 |
|  | 11 kV Auto Switched Capacitor Bank |  | Nos | 2 |
|  | 66 kV 3CX300 sqmm XLPE insulated, stranded aluminum conductor, HDPE outer sheath Power cable | For connecting all power Transformer from 66 kV Trafo panel | Lot | 1 |
|  | 11 kV 1CX1000 sqmm XLPE insulated, stranded Aluminium conductor, PVC outer sheath cable | All four Power transformer to 11 kV incoming Panel | Lot | 1 |
|  | 11 kV 3CX300 sqmm XLPE insulated, stranded aluminum conductor, PVC outer sheath Power cable | For 11 kV Capacitor Bank | Lot | 1 |
|  | GIS termination kit for 66kV, 3C x 300 sqmm cable | For termination at 66kV GIS | Nos | 6 |
|  | End Termination kit for 66kV, 3CX300 sqmm Cable | For connecting cable to the bushing of power Transformers | Nos | 6 |
|  | End termination kit for 11kV, 1c x 1000sqmm cable | - For Terminating 11 kV Cables at all 11 kv incomer end - For Terminating 11 kV Cables at all Transformer end | Set | 36 |
|  | End Termination kit for 11kV, 3c x 300sqmm cable | For Terminating 11 kV Cables at 11 kV Capacitor Bank end and 11 kV Capacitor Panel end | Nos | 8 |
|  | Fire Resistant Coating | - On all cable specified in “Grid S/S Scope of supply” - Fire rating-4 hours | Lot | 1 |
|  | Cable Sealing System | For all cables entering and exiting the proposed Substation Building | Lot | 1 |
|  | Cable Support Structure | Mounting cable for Power Transformers , Switchgear etc. | Lot | 1 |
|  | Clamps, Connectors & Accessories |  | Lot | 1 |
|  | Insulating Sleeves | For 66 kV and 11 kV side Transformer bus bars | Lot | 1 |
|  | Shrouds | For Bare Conductors | Lot | 1 |
|  | AC Distribution Board |  | Nos | 1 |
|  | DC Distribution Board |  | Nos | 1 |
|  | 220 VDC Li Ion Battery Bank (150 AH) |  | Nos | 1 |
|  | SMPS Based Battery Charger |  | Nos | 1 |
|  | 400 kVA Station Transformer |  | No | 1 |
|  | Control Cables with proper ferruling and tagging along with glands and lugs | For items specified in “Grid S/S Scope of supply” including interlocks | Lot | 1 |
|  | LT Power Cable | For items specified in “Grid S/S Scope of supply” | Lot | 1 |
|  | Insulated Floor Coating | For Switchgear Room, Battery Bank Room, ACDB, DCDB Room | Lot | 1 |
|  | Cable Tray including bends | - For routing Power, LT and Control Cables - For items specified in “Grid S/S Scope of supply” - 50% spare capacity in each is tray is required | Lot | 1 |
|  | Complete Grid Earthing | Earthing of all Grid Substation and items specified in “Grid S/S Scope of supply” | Lot | 1 |
|  | Fire protection system | For items specified in “Grid S/S Scope of supply” | Lot | 1 |
|  | Illumination and lighting system with Associated Structure |  | Lot | 1 |
|  | Exhaust and Ventilation system | For Substation Building | Lot | 1 |
|  | Lightning Protection | For Complete Grid S/S | Lot | 1 |
|  | Conduits | For Lighting, Ceiling Fans, Power Sockets, Exhaust Fans, etc. | Lot | 1 |
|  | SF6 Multi analyzer |  | No | 1 |
|  | Material for Civil Works |  | Lot | 1 |
|  | RTU and Associated SCADA Works |  | Lot | 1 |
|  | EOT Crane |  | Lot | 1 |
|  | Painting of Feeder names (SCADA code, Asset Code, etc) | As per Engineer Incharge Guidance | Lot | 1 |
|  | Licensed programming software and communication cord for offered numerical relays |  | No | 1 |
|  | Tools |  |  |  |
|  | Special Tools | Corresponding to Items specified in " Grid S/S Scope of supply " for ease of Operation and Maintenance | Lot | 1 |
|  | High voltage Test Set |  | No | 1 |
|  | Insulation Resistance Kit |  | No | 1 |
|  | Earthing Rod for Discharging Purpose |  | No | 1 |
|  | Live Line Detector |  | No | 1 |
|  | Bosch Professional Tool Kit |  | No | 1 |
|  | Portable Flash Light |  | No | 1 |
|  | A-Type ladder (3 feet height) to be supplied.( For viewing and operating Relays) |  | No | 1 |
|  | Stepped Trolley cum platform | To access Relays of Switchgears | No | 1 |
|  | Recommended/Mandatory Spares as per Specification of Supplied Items |  | Lot | 1 |
|  | Drinking Water Cooler | Water Purification Technology shall be RO | No | 1 |
|  | 9 Meter SMC Expandable Ladder |  | No | 1 |
|  | SLD of Grid | Covered in Acrylic Sheet | No | 1 |
|  | Video surveillance system |  | Lot | 1 |
|  | Emergency Exit Floor Marking | For Proposed Building | Lot | 1 |
|  | Air Conditioning | For Control Room and RTU | Lot | 1 |

### GRID S/S SCOPE OF WORK

- Broad scope of work is specified below. Refer respective equipment/work specifications for detailed scope of work.

| S. No | Items | Remarks | Unit | Qty |
| --- | --- | --- | --- | --- |
|  | Erection, Testing and Commissioning of all items specified in “Grid S/S Scope of supply” |  | Lot | 1 |
|  | Retrofitting Work of Differential Relay at both receiving and sending end | - Erection, testing and commissioning - Cut out of switchgears for Relay erection purpose - Control cable works | Lot | 1 |
|  | Soil Resistivity Test | For earthing Design | No | 1 |
|  | Training on O&M of 33 KV GIS | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Training on application, programming, testing and commissioning of Numerical Relays | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Training on commissioning, operations and maintenance of 11KV Switchgear | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Training on commissioning, operations and maintenance of NIFPS | One day classroom training at BYPL Training Centre and one day onsite training. Training shall be provided by Domain experts only | Days | 2 |
|  | Civil Works | Refer Specification for Civil Works |  |  |
|  | Site survey, Soil testing, design and engineering |  | Lot | 1 |
|  | Substation Building | Building shall be G+1 storey. However, if it is not possible to accommodate the equipment on G+1 storeys due to space constraint at site, G+2 storey shall be constructed to accommodate the equipment | No | 1 |
|  | Cable cellar at ground floor |  | No | 1 |
|  | 11kV switchgear room at First Floor |  | No | 1 |
|  | 66/33kV GIS Room at First floor |  | No | 1 |
|  | EOT Crane for 66kV GIS Room | Capacity shall be based on heaviest package with appropriate safety margin. Minimum capacity shall be 5 tons | No | 1 |
|  | Control Room at First Floor | For housing CRP, ACDB, DCDB, RTU etc | No | 1 |
|  | Battery Room at First Floor |  | No | 1 |
|  | Maintenance Room at First Floor |  | No | 1 |
|  | Pantry at First floor |  | No | 1 |
|  | Washroom at First Floor |  | No | 1 |
|  | Two side entry and exit |  | Lot | 1 |
|  | Fire retardant windows and doors | Fire rating for 2 hours withstand | Lot | 1 |
|  | Motorized Shutter | For Entry and Exit of Switchgears | No | 1 |
|  | Table |  | No | 2 |
|  | Chair |  | No | 6 |
|  | MS Almirah |  | No | 3 |
|  | Water tank and booster pump |  | Lot | 1 |
|  | Yard Works |  |  |  |
|  | Foundation Works | For all equipment included in “Grid S/S Scope of supply” | Lot | 1 |
|  | Levelling for compete plot area |  | Lot | 1 |
|  | Boundary wall with Barbed Wire |  | Lot | 1 |
|  | Power Cable Trench | With 50% spare capacity for future use | Lot | 1 |
|  | Control Cable Trench | With 50% spare capacity for future use | Lot | 1 |
|  | Support Structure and appropriate clamping arrangement | For proper termination of all power and control cables | Lot | 1 |
|  | Chequered Plate for trenches |  | Lot | 1 |
|  | Motorized De-Watering system for trenches |  | Lot | 1 |
|  | Sump Pit | - Joining of all Power Transformer with Respective Soak Pit - Capacity shall be 20000 Liters - Motorized Dewatering/ De-oiling for Sump Pit | No | 1 |
|  | Soak Pit | For All Power Transformers | No | 2 |
|  | Fire Walls | For power transformers | Lot | 1 |
|  | Fencing | - For all outdoor equipment - Pre-galvanized MS Fencing with powder coating - Fencing shall be Anticut and anticlimb type | Lot | 1 |
|  | Main Gate | MS gate of size 6.5m | No | 2 |
|  | 6m Road | Between Gates, Substation Building, Power Transformers, Station Transformer, Auto Switched Capacitor Bank | Lot | 1 |
|  | Yard Development | For Complete outdoor Yard Area | Lot | 1 |
|  | Rain Water Harvesting |  | No | 1 |
|  | Guard Room |  | No | 1 |
|  | Drainage and Sewage System |  | Lot | 1 |

### GRID S/S SLD

### OUTGOING SCOPE OF SUPPLY

| S No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Cable 11 kV 3Cx300 sq mm | Meter | 18350 |
|  | Cable Indoor End Termination kit suitable for 11 kV 3Cx300 sq mm cable (Make-Raychem/3M/Yamuna Power Infrastructure) | No's | 22 |
|  | Cable straight through joint kit suitable for 11 kV 3Cx300 sq mm cable (Make-Raychem/3M/Yamuna Power Infrastructure) | No's | 61 |
|  | Motorized RMU along with FRTU, Battery Bank and Battery Charger Indoor - 4 Way | No's | 6 |
|  | Motorized RMU along with FRTU, Battery Bank and Battery Charger Outdoor - 3 Way | No's | 5 |
|  | Precast RCC (1:2:4) cable cover 600x300x50 mm | No's | 25996 |
|  | HDPE PIPE 180 MM DIA PN6 PE 80 | Meter | 6423 |
|  | HDPE Pipe Collar 180 mm | No's | 1070 |
|  | RCC coffin for straight through Joint | No's | 61 |
|  | RCC Plate for straight through Joint | No's | 61 |
|  | Weather and acid resistant PVC warning tape of 150mm width 300 micron thick Yellow colour with desired Red/Black printing. | Meter | 15598 |
|  | Route indicating stone at every 50 meter circuit length and Joint indicating stones at every cable joint location | No's | 428 |
|  | Galvanized Channel, Angle, Beam and other Structural steel with hardwares for all structures including cable support Structure | MT | 1 |
|  | Fine Sand | Cubic meter | 1685 |
|  | End Cap for Cable 11 KV AL 3X300 Sqmm XLPE | No's | 122 |
|  | HDPE cleat with hardware's suitable for 11 kV 3Cx300 sq mm cable | No's | 12 |
|  | Danger Plates | No's | 6 |
|  | Circuit Name Plate | No's | 6 |
|  | Cable Identitication Road Stud | No's | 1 |
|  | Aluminium Cable Identification tag with nylon string | No's | 612 |
|  | Safety barricading PVC tape | Meter | 1 |
|  | Safety barricading cone | No's | 1 |
|  | RFID based electronic buried type cable route marker for cable joints and turns having facility to feed the joint/turn related information | No's | 1 |
|  | Galvanized Nuts & Bolts | Kg | 1 |
|  | Coarse sand for PCC & RCC | Cubic meter | 1 |
|  | Burnt clay Brick - First class | No's | 1 |
|  | Cement Bags 50 kg | No's | 1 |
|  | Reinforcement steel bars | MT | 1 |
|  | Construction Aggregate | Cubic meter | 1 |
|  | Chemical earthing kit (3 Meter Cu Bonded Rod, Chemical, Polyplastic Pit cover | Lot | 1 |
|  | Cu bonded rod for mesh formation of earthing | Lot | 1 |
|  | Phase marking Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) | Lot | 1 |
|  | cable sheath repair 3M Scotch 2228 Rubber mastic Tape | Lot | 1 |
|  | Self-Fusing Silicone Rubber Electrical Tape 70 | Lot | 1 |
|  | Fire retardant coating for application on outgoing Power cables | Lot | 1 |

### OUTGOING SCOPE OF WORK

| S No | Items | UOM | Qty |
| --- | --- | --- | --- |
|  | Surveying of cable Route, Detailed Site Plan & Profile using Ground penetration Radar System, Excavation of trial pits as per field requirement, preparation of route drawing with location of joint chambers position and finalizing the cable route in consultation with BSES Representative | Meter | 18350 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Ordinary Bituminous/C.C.Road (including dewatering if any) | Cubic meter | 1936 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Dense Carpeted bituminous Road (including dewatering if any) | Cubic meter | 1549 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Footpath/tile/Rajasthani Stone/Brick work (including dewatering if any) | Cubic meter | 1549 |
|  | Digging of cable trench as per specification and drawings. Rate is inclusive of digging and backfilling for Hard Rocky Soil (including dewatering if any) | Cubic meter | 1549 |
|  | Laying of XLPE cables in the excavated trench, as per BYPL Standards (Regarding Depth, Layer formation, etc). Cable rollers to be used during Laying. | Meter | 11928 |
|  | Laying of XLPE cable in HDPE/Hume/GI in excavated trench | Meter | 3670 |
|  | Laying of cable in trenchless ducts including laying of cable and HDPE pipe using HDD machine including laying of 200 mm dia HDPE pipe PN4 PE 80 Class | Meter | 2753 |
|  | Continuous steel Barricading for all Excavated areas, till the work is completed. | Meter | 15598 |
|  | Fixing of Aluminum Cable identification tags with Nylon string at every 30 Mtrs cable length | No's | 612 |
|  | Installation of straight through joints for 11 kv 3Cx300 sq mm cables by jointing kit OEM authorized jointer | No's | 61 |
|  | Instalation of End Termination kit for 11 kV 3Cx300 sq mm cable by jointing kit OEM authorized jointer | No's | 22 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Ordinary bituminous road/C.C. Road | No's | 15 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Dense carpeted bituminous road. | No's | 15 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Footpath/ tile/ Rajasthani Stone / Brick Works | No's | 15 |
|  | Digging of joint pit suitable for 11 cable joint box and covering the joint box with sand and providing protection for Hard Rocky Soil. | No's | 16 |
|  | Spreading of sand forming cushion and cover around the cable | Cubic meter | 1685 |
|  | Disposal of debris/surplus malba including Loading / Unloading | Cubic meter | 1853 |
|  | Digging of test pits of required size( not less than 1/2 Meter Wide at site for identification of cable route) | No's | 2 |
|  | Watch and ward of complete circuit till project handover | Lot | 1 |
|  | Installation of precast RCC Cable cover | No's | 25996 |
|  | Installation of Route and Joint indicating stone marked with "BYPL 11 KV Cable Helpline No-91-11-399 99 808" | No's | 428 |
|  | Laying of PVC warning tape | Meter | 15598 |
|  | Fabrication and installation of galvanized channel, angel, Beam and other structural steel including nuts & bolts for all structures including cable support structure | MT | 1 |
|  | Partial discharge test on complete cable length at site | Lot | 1 |
|  | VLF High voltage test & Tan Delta test on complete cable length as per relevant IEC/IEEE | Lot | 1 |
|  | Installation, mounting and fixing of 11 kV 3Cx300 sq mm cable with termination on mounting structure/tower and fixing it with suitable HDPE cleats | No's | 12 |
|  | Fixing of danger plate on poles including fabrication of clamps etc | No's | 6 |
|  | Fixing of circuit Name plate including fabrication of clamps etc | No's | 6 |
|  | Installation of Cable identification road stud | No's | 1 |
|  | Submission of actual laid drawing of cable circuits including GPS coordinates of all joint in cables circuits | No's | 2 |
|  | Cable Phasing work, Cable Phase Sequence (R,Y,B) Marking, Cable 1&2 Marking, and final connection as per Phase Sequence. | No's | 4 |
|  | Masonry Brick work | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:1.5:3 (1 cement :1.5 coarse sand : 3 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:2:4 (1 cement :2 coarse sand : 4 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Providing and laying in position cement concrete 1:4:8 (1 cement :4 coarse sand : 8 graded stone aggregate) excluding the cost of centering, shuttering, finishing and enforcement | Cubic meter | 1 |
|  | Centering, shuttering including shuttering propping etc and removal of shuttering | Lot | 1 |
|  | Fabrication of reinforcement for RCC work including straightening, cutting, bending, placing in position and binding all complete thermo mechanically treated bars. | Lot | 1 |
|  | Installation of Brick as Cable Separator | No's | 1 |
|  | ETC of RFID Active Marker | No's | 1 |
|  | Installation of RCC Coffin for Cable Joint | No's | 61 |
|  | Installation of RCC Plate for Cable Joint | No's | 61 |
|  | Application of Scotch Vinyl Electrical Tape 35 (Red, Yellow and Blue) on cable end termination kit | Lot | 1 |
|  | Application of 3M Scotch 2228 Rubber mastic Tape on cable straight through joint end sealing and for cable sheath repair | Lot | 1 |
|  | Application of Self-Fusing Silicone Rubber Electrical Tape 70 on cable end termination boot and lug | Lot | 1 |
|  | Application of fire retardant coating on outgoing Power cables in yard boundary and exposed areas | Lot | 1 |
|  | ETC of Motorized RMU along with FRTU, Battery Bank and Battery Charger Indoor - 4 Way | No's | 6 |
|  | ETC of Motorized RMU along with FRTU, Battery Bank and Battery Charger Outdoor - 3 Way | No's | 5 |
|  | ETC of earthing work | Lot | 1 |

## SCOPE DEMARCATION

| S. No | Head | BYPL | Bidder's Scope | Remarks |
| --- | --- | --- | --- | --- |
|  | Road Cutting Permission and Road Restoration |  |  | Statutory fees will be borne by BYPL |
|  | Permissions from Various External and Internal Agencies Regarding Cable Laying and Commissioning(Traffic Police, GAIL, IGL, DJB,MTNL/BSNL etc) |  |  | Statutory fees will be borne by BYPL |
|  | PTCC Permission from Various External Agencies (Telecom, DTL. Railways, Defense, etc) |  |  | As per specifications & Standards |
|  | Continuous Steel Barricading with Mobile no of Vendor's Engineer Incharge |  |  | Steel barricade should have small scheme description along with vendor and BYPL name on it |
|  | Permit to work request to BYPL authority |  |  | Permit Should be applied to Engineer Incharge prior to work through proper procedure |
|  | Permit to work issuance from BYPL authority |  |  |  |
|  | Testing Equipments |  |  |  |
|  | Lighting Arrangement |  |  |  |
|  | Construction Power and Construction Water |  |  |  |
|  | Safety and Security of Manpower( Labor, Engineers, Supervisors etc) |  |  |  |
|  | Various Tools and Tackles related to Job |  |  |  |
|  | Loading, Unloading and Transportation of Material |  |  | It includes transportation of dismantled equipment to BYPL store in stacked manner. |
|  | Cleanliness around work premises |  |  |  |
|  | Document/Drawing Submission |  |  |  |
|  | Document/Drawing Approval |  |  |  |
|  | Security and Safety of material until handover |  |  |  |
|  | Various Machines e.g. Crane, Hydra, JCB etc to complete the Job |  |  |  |
|  | Maintenance of Equipments Until Handover to Engineer Incharge and EHV O&M |  |  |  |
|  | Electrical Inspector Clearance |  |  | Only statutory fees will be borne by BYPL |
|  | Permit issuing agency for Works inside BYPL Premises |  |  |  |
|  | Permit requesting Agency |  |  | Permit Should be applied to Engineer In charge prior to start of work. Isolation & permit of only one Feeder at a time, shall be given at a time, during final hook up. All necessary preparation works to be made, in order to minimize the Shutdown Time. |
|  | Temporary office near work premises |  |  | After handing over the equipments, contractor has to evacuate the premises within one week otherwise deemed fit action will be taken |
|  | Temporary store near work premises |  |  |  |
|  | Yard aesthetics at work place should be maintained at the time and after the completion of Work |  |  | Disposal of Scrap/Debris etc from site and complete cleaning of working area till handover |
|  | Any damages done to the existing system, shall be repaired/ rectified/ replaced |  |  |  |
|  | Clearance certificate |  |  | Clearance Certificate shall be taken from BYPL Departments (Quality, Safety, Protection, O&M, SCADA, EHV, Civil, etc ) before Final Charging of the Systems. Any Site Observations/ Punch points, observed during execution, shall be attended. |
|  | Various compliances pertaining to Job |  |  | IE rules, CEA Regulation 2010 |

## DOCUMENTATION

- Document checklist for each stage is given in table below. (Refer equipment specification for details)

- Document check sheet compliance shall be the first sheet for each submission stage i.e. Technical bid, Drawing Approval, Pre Dispatch, Pre closure.

- No submission is acceptable without check list compliance.

- Deficient/ improper document/ drawing submission shall be liable for rejection.

- Order of documents shall be strictly as per the check list.

- Any drawing not included in the below table but necessary for detailed engineering shall be deemed to be included in bidder’s scope.

| S. No. | Description | Technical Bid | Drawing Approval | Pre-Dispatch | Pre-Closure |
| --- | --- | --- | --- | --- | --- |
|  | Tender No. | Required |  |  |  |
|  | Communication Details |  |  |  |  |
|  | Name of the Bidder | Required |  |  |  |
|  | Name of Authorized contact person | Required |  |  |  |
|  | Contact No. of Authorized contact person | Required |  |  |  |
|  | E-mail id of Authorized contact person | Required |  |  |  |
|  | Document Submission Format |  |  |  |  |
|  | Documents shall be submitted in Box file/spiral binding. Any other format is not acceptable | Required |  |  |  |
|  | Index of documents with page numbers for each document | Required |  |  |  |
|  | Separator with document description shall be provided before each document | Required |  |  |  |
|  | Qualifying Requirement Compliance |  |  |  |  |
|  | Summary of compliance of qualifying criteria in tabular form along with summary of documentary proof provided | Required |  |  |  |
|  | Detailed Documents supporting compliance of qualifying criteria | Required |  |  |  |
|  | Drawings/ Documents as per Technical Specification. |  |  |  |  |
|  | Signed copy of technical specification | Required |  |  |  |
|  | Type Test reports of offered model/ type/ rating | Required | Required |  |  |
|  | Sheath integrity test results for every cable section duly stamped and signed by BSES representative |  |  |  | Required |
|  | VLF, Tan delta and Partial discharge test results for every circuit duly stamped and signed by BSES representative |  |  |  | Required |
|  | OFC cable Test results for every circuit duly stamped and signed by BSES representative |  |  |  | Required |
|  | Actual as laid drawing of complete circuit with GPS coordinates at every a) 30 meter circuit length b) Cable joints c) Every turn/curve d) Every road crossing (both ends) Drawing shall be submitted in hard copy (minimum A3 Size) and AutoCAD dwg |  |  |  | Required |
|  | Deviation Sheet | Required | Required |  |  |
|  | Detailed Drawings | Required | Required |  |  |
|  | Other drawing/ documents mentioned in technical specification | Required | Required |  |  |
|  | Soft copy of complete technical bid in pen drive | Required |  |  |  |
|  | Samples as per technical specification. | Required |  |  |  |
|  | Design Calculation |  | Required |  |  |
|  | Manufacturer's quality assurance plan |  | Required |  |  |
|  | GTP |  | Required |  |  |
|  | Inspection Reports |  |  | Required |  |
|  | As manufacturing Drawings |  |  | Required |  |
|  | Operation and Maintenance Manual |  |  | Required |  |
|  | As built Drawings |  |  |  | Required |
|  | Soft Copy |  |  |  |  |
|  | In Pen drive | Required |  |  |  |
|  | Through Mail |  | Required | Required | Required |

# APPROVED MAKE LIST

- Following table contains Approved Make List. Although, Any make other than specified in table shall be subject to BSES Yamuna Power Limited Approval.

| S. No | Equipment | MAKE |
| --- | --- | --- |
|  | 66 kV Power Cable | Universal/KEI/Sterlite |
|  | 33 kV & 11 kV Power Cable | Universal/KEI/GEMSCAB/Polycab/Torrent/Sterlite/Gupta Power/KEC |
|  | 66 kV & 33 kV Cable Straight through & end termination jointing kit | Raychem/3M |
|  | 11 kV Cable Straight through & end termination jointing kit | Raychem/3M/Yamuna Power Infrastructure |
|  | Control cable | Universal/KEI/GEMSCAB/Polycab/ Cords Cable |
|  | Power Transformer | ABB/Schneider/Siemens/Transformer & Rectifiers/ EMCO/ Bharat Bijlee/ BHEL/Toshiba/Voltamp/CGL |
|  | 66 kV GIS | ABB/Siemens/Schneider |
|  | 33 kV GIS | ABB/Siemens/Schneider |
|  | 66 kV CRP | ABB/Siemens/Schneider |
|  | 11 kV AIS | ABB/Siemens/Schneider/CGL |
|  | 11 kV Auto Switched Capacitor bank | ABB/ EPCOS/Shreem |
|  | Numerical relays | ABB (R series), Siemens (Siprotec series) and Schneider / Alstom (Micom Series) |
|  | Cable sealing system | Roxtec, MCT Brattberg |
|  | Fire retardant coating for cables | 3M/Demech/Stanvac |
|  | SF6 Multi Analyser | Dilo/Wika |
|  | Floor coating | 3M/Demech/Stanvac |